E90 Online UPS

10kVA, 15kVA, 20kVA Models

Service Manual

www.xpcc.com | © 2018 Xtreme Power Conversion Corporation. All rights reserved. (Rev 8/13/18)

Table of Contents

Important Safety Instructions.......................................................................3

Product Description.....................................................................................6

Summarization................................................................................................................................6

Functions and Features...................................................................................................................6

Installation......................................................................................................................................7

E90 Cabinet View Outlook.............................................................................................................10

LCD control Panel..........................................................................................................................13

Installation Notes..........................................................................................................................13

External Protective Devices...........................................................................................................14

Power Cables.................................................................................................................................14

Power Cable Connection...............................................................................................................15

Battery Pack Connection................................................................................................................17

UPS parallel Installation ...............................................................................................................25

Operation..................................................................................................27

Operation Modes.........................................................................................................................27

Turn on/off UPS.............................................................................................................................30

The LCD Display.............................................................................................................................32

Parallel system commissioning......................................................................................................42

Display Messages/Troubleshooting...............................................................................................43

Options ......................................................................................................................................... 45

Specifications............................................................................................47

Problems and Solution..............................................................................48

USB communication port definition.............................................................49

RS232 communication port definition........................................................50

RS485 communication port definition........................................................51

BAT_T communication port definition........................................................52

REPO instruction........................................................................................53

Obtaining Service.......................................................................................54

Xtreme Power Conversion Limited Warranty...............................................55

Product introduction

Summary

E90 Series is a kind of high-frequency online intelligent UPS and adopts double DSP control chips, advanced control

technology and double conversion topology. It eliminates various interference of the grid and makes the output

a stable and pure sine wave power with low noise, no interference and low distortion. With strong load capac-

ity, good load compatibility, wide input voltage and frequency range, excellent generator compatibility and zero

transfer time, it greatly meets the requirement of variety of applications. Comprehensive protection enhances the

stability and reliability of the system. Intelligent battery management, equalized and floating charging auto conver-

sion, battery discharge time prediction and battery self-test can extend the battery life. It can be used in advanced

network systems.

- power range:10KVA-20KVA, up to 4 units can be parallel,

- working mode:High frequency intelligent online (3-phase in to 3-phase out)

- application: Work station, network server, and computer rooms and data center

Features

Three-phase UPS

This E90 series is three-phase in to three-phase out UPS with a large capacity, the three phase input current is

balanced which can balance the load of each phase.

Digital control

Digital control is used for all parts of the UPS, which makes the performance indicators very excellent and the

system more stable. It not only has self-protection and fault diagnosis, but also can avoid risks of analog device

failure, which allows the control system more reliable.

Settable charging current

By setting the battery capacity configured by user, the reasonable charging current can be automatically allo-

cated. Constant voltage charging mode, constant current charging mode and floating charging mode can auto-

switch smoothly.

Intelligent charging method

Advanced two-way, three-stage charging method is adopted. At the first stage, fast recharge with constant large

current to 90% capacity; at the second stage, constant voltage charge can activate the battery characteristics and

make the battery full; at the third stage, floating mode operates. This method can provide a balance between the

fast charge and extended the battery life, which saves the battery investment.

LCD display

Both the LCD and LED display for the series allows the users a more intuitive understanding of the UPS status and

operating parameters such as input/output voltage and frequency, load capacity, battery capacity, temperature

and ect.. All the operation are under the monitoring.

Intelligent monitoring function

When the SNMP is selected with UPS, the remote monitoring can be achieved easily.

EPO function

An emergency power off(EPO) button interface Is embedded in the rear panel of the UPS. The user can add the

EPO button. In case of emergency, press the EPO button to shut down the UPS. It also has remote emergency

power off (REPO) function.

Operating panel

Operating interface

1) LED (from top to bottom: “alarm”, “bypass”, “battery”, “inverter”)

2) LCD display

3) Scroll button

4) Off button

5) On button(battery cold start switch)

Status indicator on front panel, LCD and other buttons

LCD and indicator LED on front panel, cooperate with buttons, can view all the data, information and set

parameters.

Table 1 Indicator description

| Name | Status | Description |
| --- | --- | --- |
| Alarm LED | Red on | UPS fault and alarm |
|  | Red off | UPS normal |
| Bypass LED | Green on | UPS bypass output |
|  | Green flash | Bypass abnormal or out of range, or bypass switch fail |
|  | Green off | Bypass normal, no bypass output |
| Battery LED | Green on | Battery supply power |
|  | Green flash | Battery discharge termination and pre-inform |
|  | Green off | Battery abnormal(no battery or battery fail) |
| Mains output LED | Green on | mains output |
|  | Green off | no mains output |

Table 2 Button description

| Button Name | Description |
| --- | --- |
| Cycle | Enter the menu to view the UPS data and information |
| ON | Start inverter battery cold start under the shutdown |
| OFF | Shut down inverter in Line mode and transfer to bypass(if bypass normal) ; Shut down inverter under the battery mode, UPS down; Battery cold start when off status |

System block diagram

Bps switch

EMI

EMI

mains

EMI

AC/DC

DC/DC

DC/AC

Output

output

batter

Battery fuse

CHARGER

fuse

Block diagram

As shown above, there is a bypass switch. When switch on it, the power will go to the bypass road. Then UPS will

detect the output switch and bypass voltage, frequency and phase sequence. If output switch is on, both the volt-

age and frequency of bypass are in the range, the UPS will send out bypass output commands and meanwhile the

bypass LED will be on.

Close the main switch, if the mains voltage, frequency and phase sequence are in the range, UPS will soft start. When bus voltage rises around 170V, PFC boost begins to work and the bus voltage will be up to about 200V. Inverter starts. When inverter is ready, it will transfer to inverter mode. If bypass voltage, frequency and phase sequence are normal, the inverter voltage will track the bypass power and switch to inverter output without in- terruption, or the UPS will transfer to inverter intermittently. Inverter LED on and bypass LED off, the inverter will provide power. If the battery is normal, the UPS will activate the charger to charge the battery.

UPS detects maintenance air-switch at any time. When remove the baffle of the switch, UPS will transfer to bypass status. Now close the maintenance air-switch for supplying power from bypass. When finish maintenance, the air- switch cannot be open until the UPS is in bypass, or it will cause the power down of load.

AC/DC & DC/DC principle circuit diagram

AC/DC & DC/DC principle

As shown above, A (yellow box) shows the rectifier circuit, B (blue box) shows the battery  input circuit, C (other part) shows the boost circuit. A and C form the PFC rectifier circuit while B and C form the battery boost circuit

Inverter DC/AC principle

A

B

Bypass and inverter principle

As shown above, A (yellow box) represents bypass circuit of UPS, B (blue box) shows the inverter circuit, which converts the Bus voltage into the AC output.

Charging principle

Battery

Charging Fuse

As shown above, charger reduces the Bus voltage to a suitable voltage to charge the battery.

Parameters

UPS specification

| MODEL NUMBER |  | E90-10K | E90-15K | E90-20K |
| --- | --- | --- | --- | --- |
| CAPACITY | Power rating | 10kVA/10kW | 15kVA/15kW | 20kVA/20kW |
| INPUT | Voltage / Range | 208Y/120VAC or 220Y/127VAC / 125-275VAC three-phase* |  |  |
|  | Frequency | 40–70Hz auto-sensing |  |  |
| OUTPUT | Voltage / Regulation | 208/120VAC or 220/127VAC / ± 1% three-phase |  |  |
|  | Frequency | 50/60±0.1% |  |  |
|  | Overload capacity | 150% for 1 min, 125% for 10 min, 110% for 60 min |  |  |
|  | Efficiency | Up to 94% online mode or 98% ECO mode |  |  |
| BATTERY | Battery Type | Sealed maintenance-lead acid |  |  |
|  | Battery quantity | Up to (60) 12V 9AH |  |  |
|  | Charger Voltage / Current | 273VDC / 1A-20A (max) programmable from LCD |  |  |
| PHYSICAL | Dimensions (W x D x H) | 9.8 x 39.2 x 34.0 in |  |  |
|  | Input / Output | Terminal blocks |  |  |
|  | Weight | 296 lbs (1 string) | 419 lbs (2 string) | 539 lbs (3 string) |
| OPTIONAL BATTERY PACK | Model | EBP80-63A | EBP80-125A |  |
|  | Battery quantity and size | (80) 12V 9AH |  |  |
|  | Dimensions (W x D x H) | 9.8 x 39.2 x 34.0 in |  |  |
|  | Weight | 535 lbs |  |  |
| ENVIRONMENT | Operating temperature | 32–104°F (0–40°C) |  |  |
|  | Audible noise | <55dB from 1M distance for 10/15kVA; <58dB from 1M distance for 20kVA |  |  |
|  | Altitude | 5,200 ft above sea level** |  |  |
| APPROVALS |  | UL, FCC, Energy Star |  |  |
| WARRANTY |  | 2 years electronics, 2 years battery warranty (USA and Canada) |  |  |
| COMMUNICATIONS INTERFACE |  | RS-232, EPO, RS485, USB, dry contact, (2) slots for optional cards (Web/SNMP, Relay/dry contact) |  |  |
| INCLUDED IN BOX |  | User manual, RS-232 communication cable, USB cable, Muser monitoring software |  |  |
| AVAILABLE OPTIONS |  | External maintenance bypass, output distribution, external battery packs, parallel cables |  |  |

*Depending on load level. **Battery life is reduced above 30°C, UPS capacity derates above 40°C and 5,200 ft above sea level

E90 Cabinet View Outlook

Front View	Side View	Rear view

10kVA Rear View (without terminal block cover)

| (1)LCD panel | (2) Intelligent Slot 1 (SNMP card/ Relay card) |
| --- | --- |
| (3)Intelligent Slot 2 (SNMP card/ Relay card) | (4) Optional dry contact output port |
| (5)Power Switch | (6) USB port |
| (7) RS485 port | (8) RS232 |
| (9) O/P Switch | (10) Maintenance switch & its cover |
| (11) Bypass Switch | (12) Terminal block for Input, output & GND |
| (13) EPO switch | (14) REPO port |
| (15) Parallel port 2 | (16) Parallel port 1 |
| (17) I/P Switch | (18) Terminal block for battery |

15-20kVA Rear View (without terminal block cover)

| (1)LCD panel | (2) Intelligent Slot 1 (SNMP card/ Relay card) |
| --- | --- |
| (3)Intelligent Slot 2 (SNMP card/ Relay card) | (4) Optional dry contact output port |
| (5)Power Switch | (6) USB port |
| (7) RS485 port | (8) RS232 |
| (9) O/P Switch | (10) Maintenance switch & its cover |
| (11) Bypass Switch | (12) Terminal block for Input, output & GND |
| (13) EPO switch | (14) REPO port |
| (15) Parallel port 2 | (16) Parallel port 1 |
| (17) I/P Switch | (18) Terminal block for battery |

Internal view of UPS

PFC power board

EPO interface board

Fan	INV power board

Input board

UPS left view

Output breaker Maintenance switch Input breaker

Input filter ring

Batteries

Battery fuse

UPS right view

INV inductor board

Output EMI board

PFC drive board

PFC inductor board

UPS module inside view (20KVA)

PFC inductor board(10-15KVA)

6pcs PFC inductors

2pcs charging

inductors

PFC inductor board(20KVA)

PFC drive board

Charging fuse	IGBT drive board

PFC power board

6pcs inv. inductors

3pcs inv. capacitors

3pcs inverter fuse

3pcs inverter SCR

drive board

BUS capacitor

Inverter inductor board

Radiator

Auxiliary power

INV. Power board

Control detection board

Output EMI board

Input EMI board(15-20KVA)

Input board

Input filter inductor board

Input fuse board

Adapter

RJ45 interface board

EPO interface board

USB interface board

PCB boards and their signals

PFC inductor board

Function overview

- Mains rectifier

- Battery input circuit

- Bypass static switch

- Boost inductor circuit

- Charging inductor circuit

Input and output interface definition

PFC inductor board interface

PFC inductor board

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| P8 | BAT- BAT- input | Name:blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | BAT- | BAT- input |
| P6 | Assistant power 15V+ | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | Assistant power | 15V+ |
| J1 | PFC drive board signal | Name: neilsbed Description: 1121S-6P P=3.96mm 180° single row square PIN white |  | PFC drive board signal |
| P15 | relay/SCR drive signal | Name: neilsbed Description: 301S-10P P=2.54mm 180° two rows square PIN black |  | relay/SCR drive signal |
| P5 | BAT+ BAT+ input | Name: blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | BAT+ | BAT+ input |
| P7 | BPS_A_IN Bps A phase input | Name:blade terminal Description:4PIN 10A M4screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | BPS_A_IN | Bps A phase input |

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| P21 | CHARGE+ CHARGE- Charging volt- age sample | Name:blade terminal Description: 1121S-3P P=3.96mm 180° single row square PIN white | CHARGE+ CHARGE- | Charging voltage sampling |
| P27 | N Neutral | Name: blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | N | Neutral |
| P20 | BPS_B_IN Bps B phase input | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | BPS_B_IN | Bps B phase input |
| P22 | BPS_C_IN Bps C phase input | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | BPS_C_IN | Bps C phase input |
| J2 | A Main A phase input | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | A | Main A phase input |
| J13 | B Main B phase input | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | B | Main B phase input |
| J14 | C Main C phase input | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | C | Main C phase input |
| J23 | A Main A phase input sampling | Name: neilsbed Description: 1121S-3P P=3.96mm 180° single row square PIN white | A | Main A phase input sampling |
| J24 | B&C Main B&C phase input sampling | Name: neilsbed Description: 1121S-3P P=3.96mm 180° single row square PIN white | B&C | Main B&C phase input sam- pling |
| J3 | positive charger SCR drive | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | CHRG_ SCR+ | positive charger SCR drive |
| J4 | Negative char- ger SCR drive | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | CHRG_ SCR- | Negative charger SCR drive |
| J9 | Negative battery SCR drive 1 | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | BAT1- SCR1 | Negative battery SCR drive 1 |

PFC drive board

Function overview:

-Bypass SCR drive circuit

-Battery SCR drive circuit

-Charging SCR drive circuit

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J11 | Negative bat- tery SCR drive 2 | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | BAT1-SCR2 | Negative battery SCR drive 2 |
| J15 | Negative bat- tery SCR drive 3 | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | BAT1-SCR3 | Negative battery SCR drive 3 |
| J8 | Positive battery SCR drive 1 | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BAT1+SCR | Positive battery SCR drive 1 |
| J10 | Positive battery SCR drive 2 | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BAT2+SCR | Positive battery SCR drive 2 |
| J12 | Positive battery SCR drive 3 | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BAT3+SCR | Positive battery SCR drive 3 |

Figure 33.PFC drive board interface

Input and output interface definition

PFC drive board interface description

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J1 | PFC drive board signal | Name: neilsbed Description: 1121S-6P P=3.96mm 180° single row square PIN white |  | PFC drive board signal |
| J13 | positive charger SCR drive | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | CHRG_SCR+ | positive charger SCR drive |
| J14 | negative charger SCR drive | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | CHRG_SCR- | negative charger SCR drive |
| J9 | negative battery SCR drive1 | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | BAT1-SCR1 | negative battery SCR drive1 |
| J11 | negative battery SCR drive2 | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | BAT1-SCR2 | negative battery SCR drive2 |
| J12 | negative battery SCR drive3 | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | BAT1-SCR3 | negative battery SCR drive3 |
| J23 | bypass SCR drive signal | Name: neilsbed Description: 2001S-2P P=2.54mm 180° single row square PIN white | BPS_B_RLY | bypass SCR drive signal |
| J6 | positive battery SCR drive1 | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BAT1+SCR | positive battery SCR drive1 |
| J7 | positive battery SCR drive2 | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BAT2+SCR | positive battery SCR drive2 |
| J8 | positive battery SCR drive3 | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BAT3+SCR | positive battery SCR drive3 |
| J2 | A phase bypass SCR1 drive | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BPS_A_SCR1 | A phase bypass SCR1 drive |
| J3 | A phase bypass SCR2 drive | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BPS_A_SCR2 | A phase bypass SCR2 drive |
| J4 | B phase bypass SCR1 drive | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BPS_B_SCR1 | B phase bypass SCR1 drive |
| J5 | B phase bypass SCR2 drive | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BPS_B_SCR2 | B phase bypass SCR2 drive |
| J10 | C phase bypass SCR drive1 | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BPS_C_SCR1 | C phase bypass SCR1 drive |

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J20 | C phase bypass SCR drive2 | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | BPS_C_ SCR2 | C phase bypass SCR2 drive |

PFC power board

Function overview:

-Boost circuit IGBT

-Charging circuit MOSFET

-Battery soft start resistor

Input and output interface definition

PFC power board interface

PFC power board

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| P6 | Assistant power 15V+ | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | Assistant power | 15V+ |
| P9 | BUS+ | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | BUS+ | BUS+ |
| P10 | BUS- | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | BUS- | BUS- |
| P14 | PFC/charger drive signal | 301S-30P P=2.54mm 180° two rows square PIN black horn |  | PFC/charger drive signal |
| P20 | Assistant power 15V+ | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | Assistant power | 15V+ |
| P22 | BAT+/BAT- battery cold start power | Name: neilsbed Description: 1121S-3P P=3.96mm 180° single row square PIN white | BAT+/BAT- | battery cold start power |
| J18 | BUS+/BUS- BUS+/BUS- Voltage detec- tion | Name: neilsbed Description: 1121S-3P P=3.96mm 180° single row square PIN white | BUS+/ BUS- | BUS+/BUS- |

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J25 | BAT+/BAT- BAT+/BAT- Voltage detec- tion | Name: neilsbed Description: 1121S-3P P=3.96mm 180° single row square PIN white | BAT+/BAT- | BAT+/BAT- Voltage detection |

INV. Inductor board

Function overview”

-INV LC filter

-Output current detection

-Inv. inductor current detection

Inv. Inductor board

Input and output interface definition

Inductor board interface

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| P2 | VOUT_A Output A phase | Name: blade terminal Description: 4PIN 10A M4screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | VOUT_A | Output A phase |
| P3 | BPS_A Bypass A phase Output | Name: blade terminal Description: 4PIN 10A M4screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | BPS_A | Bypass A phase Output |
| P5 | BPS_B Bypass B phase Output | Name: blade terminal Description: 4PIN 10A M4screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | BPS_B | Bypass B phase Output |
| P6 | VOUT_B Output B phase | Name: blade terminal Description: 4PIN 10A M4screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | VOUT_B | Output B phase |
| P8 | BPS_C Bypass C phase Output | Name: blade terminal Description: 4PIN 10A M4screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | BPS_C | Bypass C phase Output |

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| P9 | VOUT_C Output C phase | Name: blade terminal Description: 4PIN 10A M4screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | VOUT_C | Output C phase |
| P12 | N Neutral | Name: blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | N | Neutral |
| P25 | N Neutral | Name: blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | N | Neutral |
| P29 | N Neutral | Name: blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | N | Neutral |
| P40 | PH2_INV_FUSE-P2 B phase inv.fuse | Name: blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | PH2_INV_FUSE- P2 | B phase inv. fuse |
| P42 | PH3_INV_FUSE-P2 C phase inv.fuse | Name: blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | PH3_INV_FUSE- P2 | C phase inv. fuse |
| P44 | PH1_INV_FUSE-P2 A phase inv.fuse | Name: blade terminal Description: UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | PH1_INV_FUSE- P2 | A phase inv. fuse |
| J1 | PH1_INV_Q_ C1E2&VOUT_A A phase inv.DC com- ponent and Output voltage sampling | Name:neilsbed Description:1121S-4P P=3.96mm 180° single row square PIN white | PH1_INV_Q_ C1E2&VOUT_A | A phase inv. DC component and Output voltage sam- pling |
| J2 | PH2_INV_Q_ C1E2&VOUT_B B phase inv.DC com- ponent and Output voltage sampling | Name: neilsbed Description: 1121S-4P P=3.96mm 180° single row square PIN white | PH2_INV_Q_ C1E2&VOUT_B | B phase inv. DC component and Output voltage sam- pling |
| J3 | PH3_INV_Q_ C1E2&VOUT_C C phase inv.DC com- ponent and Output voltage sampling | Name: neilsbed Description: 1121S-4P P=3.96mm 180° single row square PIN white | PH3_INV_Q_ C1E2&VOUT_C | C phase inv. DC component and Output voltage sam- pling |
| J4 | INV SCR drive/output current detection signal | Name: neilsbed Description: 301S-26P P=2.54mm 180° two rows square PIN black horn |  | INV SCR drive/ output cur- rent detection signal |

Inverter power board

Function overview:

-Auxiliary power

-Half-bridge inverter circuit

-Fan speed regulation circuit

Inverter power board

Input and output interface definition

Inv. Power board interface

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| P9 | +DCBUS +BUS voltage | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | +DCBUS | +BUS voltage |
| P10 | -DCBUS -BUS voltage | Name: blade terminal Description: 4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | -DCBUS | -BUS voltage |
| P13 | 15V/-15V ASSISTANT POWER | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | +15V/-15V | ASSISTANT POWER |
| P28 | +24V_FAN Fan power | Name: neilsbed Description: 1121S-2P P=3.96mm 180° single row square PIN white | +24V_FAN | Fan power |
| J4 | VBPS_A/BAT+/VINV_A Supply power from auxiliary power | Name: neilsbed Description: 1121S-5P P=3.96mm 180° single row square PIN white (remove 2 4PIN) | VBPS_A/BAT+/ VINV_A | Supply power from auxiliary power |
| J5 | REC_THERMAL_ SWITCH REC temperature de- tection | Name:neilsbed Description:2001S-2P P=2.54mm 180° single row square PIN white | REC_THERMAL_ SWITCH | REC tempera- ture detection |
| J6 | upper half bridge INV drive signal | Name:neilsbed Description:301S-12P P=2.54mm 180° two rows square PIN black horn |  | upper half bridge INV drive signal |

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J7 | ASSISTANT POWER +15V/-15V | Name:neilsbed Description:1121S-4P P=3.96mm 180° single row square PIN white | ASSISTANT POWER | +15V/-15V |
| J8 | ON Start up signal button | Name:neilsbed Description:2001S-2P P=2.54mm 180° single row square PIN white | -ON | Start up signal button |
| J9 | REC_THERMAL_ SWITCH REC temperature de- tection | Name:neilsbed Description:2001S-2P P=2.54mm 180° single row square PIN white | REC_THERMAL_ SWITCH | REC tempera- ture detection |
| J10 | lower half bridge INV drive signal | Name:neilsbed Description:301S-10P P=2.54mm 180° two rows square PIN black horn | +24V_FAN | lower half bridge INV drive signal |
| J18 | +24_CSU monitoring unit POWER | Name:neilsbed Description:1121S-2P P=3.96mm 180° single row square PIN white | +24_CSU | monitoring unit POWER |

DSP board

Function overview:

-UPS control

-Communication circuit

-Parallel circuit

-Display circuit

DSP board

Input and output interface definition

Table 9 DSP board interface

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J7 | ASSISTANT POWER +15V/-15V | Name:neilsbed Description:1121S-4P P=3.96mm 180° single row square PIN white | ASSISTANT POWER | +15V/-15V |
| J1 | A phase INV voltage/ output voltage sam- pling signal | Name:neilsbed Description:1121S-5P P=3.96mm 180° single row square PIN white | Vinv_A/ Vout_A | A phase INV volt- age/output voltage sampling signal |
| J2 | B phase INV voltage/ output voltage sam- pling signal | Name:neilsbed Description:1121S-5P P=3.96mm 180° single row square PIN white | Vinv_B/ Vout_B | B phase INV volt- age/output voltage sampling signal |

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J3 | C phase INV voltage/ output voltage sam- pling signal | Name:neilsbed Description:1121S-5P P=3.96mm 180° single row square PIN white | Vinv_C/Vout_C | C phase INV voltage/output voltage sam- pling signal |
| P20 | Assistant power 15V+ | Name:neilsbed Description:1121S-2P P=3.96mm 180° single row square PIN white | Assistant power | 15V+ |
| P21 | charging voltage sam- pling | Name:neilsbed Description:1121S-3P P=3.96mm 180° single row square PIN white | CHARGE+/- | charging volt- age sampling |
| J23 | input voltage sampling | Name:neilsbed Description:1121S-3P P=3.96mm 180° single row square PIN white | Vin_A/Vin_N | input voltage sampling |
| J24 | input voltage sampling | Name:neilsbed Description:1121S-3P P=3.96mm 180° single row square PIN white | Vin_B/Vin_C | input voltage sampling |
| J26 | bypass voltage sam- pling | Name:neilsbed Description:1121S-8P P=3.96mm 180° single row square PIN white | Vbps_A/ Vibps_N/ Vbps_B/ Vbps_C | bypass voltage sampling |
| J25 | battery voltage sam- pling | Name:neilsbed Description:1121S-3P P=3.96mm 180° single row square PIN white | Vbat+/Vbat- | battery voltage sampling |
| J18 | BUS voltage sampling | Name:neilsbed Description: 1121S-3P P=3.96mm 180° single row square PIN white | Vbus+/Vbus- | BUS voltage sampling |
| J17 | parallelsignal1 | Name: neilsbed Description: 2001S-13P P=2.54mm 180° single row square PIN white |  | parallelsignal1 |
| J19 | parallelsignal2 | Name: neilsbed Description: 2001S-13P P=2.54mm 180° single row square PIN white |  | parallelsignal2 |
| J12 | monitor& communica- tion signal | Name: neilsbed Description: 2001S-13P P=2.54mm 180° single row square PIN white |  | monitor& communica- tion signal |
| CN3 | LCD display signal | Name: neilsbed Description: 302NS-16P P=2.54mm 180° two rows square PIN black |  | LCD display signal |
| P14 | PFC drive signal | Name:neilsbed Description:301S-30P P=2.54mm 180° two rows square PIN black horn |  | PFC drive signal |
| J4 | INV. inductor board INV. SCR drive/out- put current detection signal | Name:neilsbed Description:301S-26P P=2.54mm 180° two rows square PIN black horn |  | INV. inductor board INV. SCR drive/output current detec- tion signal |

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J6 | upper half bridge INV drive signal | Name:neilsbed Description:301S-12P P=2.54mm 180° two rows square PIN black horn | ASSISTANT POWER | upper half bridge INV drive signal |
| J10 | lower half bridge INV drive signal | Name:neilsbed Description:301S-10P P=2.54mm 180° two rows square PIN black horn | Vinv_A/ Vout_A | lower half bridge INV drive signal |

Output EMI board

Function overview:

-Output EMI

Output EMI board interface

Input and output interface definition

Table 10 output EMI board interface

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| P1 | N | Name:blade terminal Description:copper tinning 1PIN 10A W=6.3mm T=0.8mm | N | Neutral |
| P10 | A | Name:blade terminal Description:copper tinning 1PIN 10A W=6.3mm T=0.8mm | A | output A phase |
| P12 | B | Name:blade terminal Description:copper tinning 1PIN 10A W=6.3mm T=0.8mm | B | output B phase |
| P14 | C | Name:blade terminal Description:copper tinning 1PIN 10A W=6.3mm T=0.8mm | C | output C phase |

Input EMI board(10-20KVA)

Function overview:

-Input EMI

Figure 18.Input EMI board interface(15/20KVA) Input and output interface definition

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| P4 | N | Name:blade terminal Description:4PIN 10A M4 screw hole straight leg 8*8.4*11.1mm T0.8mm tinned copper | N | N |
| P1 | Vin-A | Name:blade terminal Description:UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | Vin-A | Input A phase |
| P2 | Vin-B | Name:blade terminal Description:UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | Vin-B | Input B phase |
| P3 | Vin-C | Name:blade terminal Description:UHTWSZ Wiring copper bar II welded assemblies plated bright nickel | Vin-C | Input C phase |

Table 11 output EMI board interface

Adapter board

Function overview:

-Signal adapter function

adapter interface

Input and output interface definition

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J24 | SNMP/ relay signal | Name:neilsbed Description:302NS-10P P=2.54mm 180° two rows square PIN black | SNMP2 | SNMP/ relay signal |
| J47 | SNMP/ relay signal | Name:neilsbed Description:302NS-10P P=2.54mm 180° two rows square PIN black | SNMP1 | SNMP/ relay signal |
| J1 | RS232/485_A signal | Name:blade terminal Description:2001S-5P P=2.54mm 180° single row square PIN white | RS232/485_A IN | RS232/485_A signal |
| J22 | 485_A signal | Name:blade terminal Description:2001S-5P P=2.54mm 180° single row square PIN white | BAT_T(485_A) | 485_A signal |
| J23 | RS232(USB) signal | Name:blade terminal Description:2001S-5P P=2.54mm 180° single row square PIN white | RS232-USB | RS232(USB) signal |
| J28 | SNMP1 signal | Name:blade terminal Description:2001S-5P P=2.54mm 180° single row square PIN white | SNMP1 IN | SNMP1 signal |
| J39 | SNMP2 signal | Name:blade terminal Description:2001S-5P P=2.54mm 180° single row square PIN white | SNMP2 IN | SNMP2 signal |

Table 12 adapter board interface

RJ45 interface board

Function overview:

-signal interface function

Figure 20.RJ45 interface board interface

Input and output interface definition

Table 13 RJ45 interface board interface

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J3 | RJ45_1 signal | Name:neilsbed Description:2001R-5P P=2.54mm 90° single row square PIN white | RJ45_1 | RJ45_1 signal |
| J4 | RJ45_2 signal | Name:neilsbed Description:2001R-5P P=2.54mm 90° single row square PIN white | RJ45_2 | RJ45_2 signal |
| J1 | RJ45_1 signal | Name:PC interface Description:RJ45 female 8PIN black 90° metal shell | RJ45_1 | RJ45_1 signal |
| J2 | RJ45_2 signal | Name:PC interface Description:RJ45 female 8PIN black 90° metal shell | RJ45_2 | RJ45_2 signal |

EPO interface board

Function overview:

-signal interface function

Input and output interface definition

EPO interface board interface

Table 14 EPO interface board interface

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| CN1 | EPO signal | Name:neilsbed Description:2001S-2P P=2.54mm 180° single row square PIN white | EPO | EPO signal |
| CN2 | EPO signal | Name:neilsbed Description:PLTBH1.5-2-S-3.8 12PIN P=3.81mm 90° square PIN green (male) | EPO | EPO signal |

EPO interface board

Function overview:

-signal interface function

USB interface board interface

Input and output interface definition

Table 15 USB interface board interface

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J1 | RS232(USB) signal | Name:neilsbed Description:2001S-4P P=2.54mm 180° single row square PIN white | EPO | EPO signal |
| J8 | Dry contact signal | Name:neilsbed Description:2001S-4P P=2.54mm 180° single row square PIN white | Dry Contact | Dry contact signal |
| J2 | RS232 signal | Name:neilsbed Description:2001S-4P P=2.54mm 180° single row square PIN white | RS232 | RS232 signal |
| USB | USB signal | Name:PC interface Description:USB interface female 6PIN black square 90° | USB | USB signal |

Parallel interface board

Function overview:

-External parallel signal interface function

Figure 23.parallel interface board interface

Input and output interface definition

Table 16 parallel interface board interface

| No. | Definition | Specification | Name | Description |
| --- | --- | --- | --- | --- |
| J5 | Parallel signal | Name:neilsbed Description:2001S-13P P=2.54mm 180° single row square PIN white | Parallel signal | Parallel signal |
| J20 | Parallel sig- nal1 | Name:PC interface Description:DB15 male P=2.29mm black 90° | Parallel signal1 | Parallel signal1 |
| J28 | Parallel sig- nal2 | Name:PC interface Description:DB15 female P=2.29mm black 90° | Parallel signal2 | Parallel signal2 |

Inspection before installation

Room environment inspection

UPS room:

UPS should be installed in a cool, dry, clean and well-ventilated environment, such as the room

temperature should be < 40°C, the humidity≤95% when 20°C, no dust on the floor, especially without

any conductive powder. The room air cannot contain acid mist or other conductive medium. For detail,

please refer to the users’ manual and other specifications.

Battery room:

The battery should be also placed in a cool, dry, clean and well-ventilated environment. The available

temperature is 15°C-25°C, typically is 20°C. The place where the battery located should keep the

constant temperature and far away from heat and vents.

UPS location inspection

The users’ manual offers the detailed installation instruction, it can be referred for installation.

Check if enough space is left for maintenance operation, ensure that the operator can still pass

through freely when the door is fully opened.

There is no obstruction in the front, above and below of UPS. Enough space should be left for

ventilation.

Air is primarily comes from front door, so check if the front door leave enough air inlet space.

UPS visual inspection

Particularly important: it is necessary to have a comprehensive inspection of internal and

external of UPS

1. Check the external power cable connection(include input /Output phase sequence

battery polarity, fasten bolt and ect.)

2. Check if the parallel cables are connected well? If they are routed separately from power cables?

3. Check if the external signal of the battery box and LBS (when needed) connections are good or

correct?

4. Check if the internal signal cable is connected well, if the cable is loosed by shaking it gently

5. Check if the internal boards or components are disconnected or damaged?

External cables and switch capacity inspection

•   For power cable selection and connection method, please refer to the user manual and related specifica-

tion.

•   Check if the breakers rated capacity of UPS input, Output and distribution cabinet are appropriate.

•   Pay attention to the Neutral and Ground protection inspection:

•   If the Neutral and Ground cable size meets the requirement?

•   Neutral has separate input and output, connect to the same Neutral is not allowed.

•   Check and confirm all the cabinets and cable ducts have been grounded according to the local provisions.

•   If the bypass has different power source, please check if the short copper-bar of the internal mains and

bypass has been removed, do the connection correctly according to the users’ manual.

•   If the battery breaker box is provided, check if the connection of it is correct.

•   Check if the UPS input/output wiring is reasonable and the cable is not in contact with any sharp edges of

objects.

•   If the user install the remote contact to realize the EPO function, make sure that the EPO cable is not inter-

ference by other main power signals to avoid UPS malfunction. About how to realize the EPO function by

remote contact, please refer to user’s manual.

•   About other control cables connection, please refer to the relevant chapters of the user’s manual.

External auto switching and generator power distribution inspection

•   Confirm that the ATS at the input side is three level switch, that is the Neutral cannot be cut off; if it is four

level, confirm that when transfer between two sources, neutral should meet on-before-off principle.

•   If the AC and generator can be selected at the input side, please confirm the proper connection between

Neutral and Ground according to the relevant specifications.

•   If the generator has dry contact, it is necessary to connect it to the generator dry contact of the monitor

board.

Battery inspection

The important security guidance when operating battery:

1) Battery exists danger of short-circuit and possibly causes burning due to the short-circuit current.

2) The voltage may reach 240VDC when battery connected in series, which has deadly danger. So keep

in mind to prevent electric shock.

3) The installation and operation of the battery must be carried out by professionals.

4) Note of eye protection to avoid accidental arc damage.

5) Remove all rings, watched, necklaces, bracelets and other metal objects.

6) The tools must be used with insulated handles.

7) Wear rubber gloves and protective aprons when do the battery operation.

8) If the battery has liquid leakage or housing damaged, place it in the ant-acid container and deal it

according to the local regulations.

9) If the electrolyte touches your skin, immediately wash it with a plenty of water.

10) The battery must be handled with reference to local environmental regulations.

Focus on the following aspects:

1) If the battery surface is clean, the appearance is damaged, deformed and leakage;

2) Check if the connection among battery is reliable, if the screws are tightened, if there is corrosion and confirm

that all battery terminals are coated with insulating material;

3) Check if there at least 10mm interval between the vertical side of the battery to ensure the free flow of the air

around the battery;

4) At least 150mm space should be left between battery top and upper frame for monitoring and maintenance of

the battery;

5) Check if the battery cabinet or battery rack installed reliably, if there is good grounded. One cable must be

individually connected between battery breaker box and UPS;

6) About connections between battery pack and UPS, battery and battery, battery pack and battery pack and

rated capacity of breaker, please refer to the user’s manual and relevant specifications;

7) Check if the wiring is reasonable and the cable is not in contact with any sharp edges of objects;

8) If the battery cabinet is installed on a raised floor, the battery power cable and breaker controlled cable can

route through the floor; if the battery cabinets are side-by-side and installed on a solid floor, cables can go into

the outlet holes at the bottom of the cabinet side to connect the battery cabinets;

9) Check and confirm that the cables are correctly and safely connected to the battery terminal blocks of the

UPS. Don’t reverse the battery. About the terminal block diagram, please refer to the user’s manual.

10) Make sure that the battery breaker box is switched off.

UPS maintenance

Guidelines for good service

The UPS is almost maintenance-free and is designed to have a failure rate less than 1% a year.

Periodical service is only needed for the fans; the UPS has a low heat generation.

A battery change after 3-6 years can be expected and, apart from the service to the fan, it should normally be the

only service done to the unit.

Due to the size of the UPS and the highly complex of the PCB, board level repair is not recommended, take the following measures instead:

Improve the reliability of the design; Replace the PCBA;

Security conditions

Warning:When the UPS is operating, all the electronic parts connected directly to the power supply and all

internal components including the battery exist high voltage. Even disconnected from the power supply, all

internal parts including the battery still have dangerous voltage (except the communication output) .

Only authorized professionals with relevant knowledge can open the machine, the others cannot open it for

maintenance.

For authorized service personnel:

Do not work alone, a second person should be standing by to assist and render help in case of accident.

Danger may occur only during the installation and maintenance. Any person operating in a normal manner is

safe.

If the UPS is in need of repair, the process A operation is recommended(This is completely safe) :Disconnect

all input power supply and battery. Load is allowed to turn off for process A. The specific steps can be seen in

chapter 3.

If the load is not allowed to turn off, please enter the maintenance bypass mode for maintenance. Follow the

process B (refer to chapter III for specific information) . Please note that the do the maintenance in maintenance

bypass mode is not absolutely safe, Part of circuits are still at work.

In maintenance mode, the load is directly connected to the power via the bypass, so the UPS will not provide any

protection.

To avoid electrostatic discharge damage, ensure that the maintenance is under the ESD safe conditions

- work on an anti-static mat;

- ground yourself and the unit when it is opened.

Be careful when disconnect the battery:

- Do not wear metal bracelets and etc.

- do not short circuit the batteries

If the UPS must be repaired during the operation such as measurement, Make sure that the power supply is isolated. In this case, a transformer can be used between the UPS and power.

Before maintenance, this manual should be entirely read.

Shutdown-disassembly/reassembly UPS

Warning: when UPS works, a large amount of energy is stored in the internal BUS capacitor, no electricity cannot

be guaranteed inside the UPS with mains isolation, so it needs extra attention when maintenance. Disconnect

all external input power of the fault machine for maintenance, After opening the case, use the bleed resistor to

release the energy stored in BUS capacitor to avoid injury to person.

3.1Please refer to the user’s manual on UPS installation content;

3.2 First read chapter 2 “Security conditions”

3.3 If the UPS is in need of repair, the process A operation is recommended(This is completely safe) :Disconnect

all input power supply and battery. Load is allowed to turn off for process A. The specific steps can be seen in

chapter 3.

If the load is not allowed to turn off, please enter the maintenance bypass mode for maintenance. Follow the

process B (refer to chapter III for specific information) . Please note that the do the maintenance in maintenance

bypass mode is not absolutely safe, Part of circuits are still at work.

In maintenance mode, the load is directly connected to the power via the bypass, so the UPS will not provide any

protection.

Step A:the load may be closed

A1 Turn off the load, disconnect all input power supply and battery;

A2 Make input/output/battery air-switch on “OFF” state

A3 Remove the right panel, left panel and top cover, do the maintenance

A4 Install the right and left panel, top cover

A5 Tighten the four screws;

A6 Connect the mains/battery/load, switch on the battery switch, press the start key to start the unit

A7 If UPS has no fault, it will has output when output switch is switched on.

A8 Switch-on the input switch, the UPS will transfer to mains, and charge the battery.

A9 Close the front door.

Step B: The load may not be closed.

B1 remove the maintenance screws and baffles to check whether the machine enter the maintenance bypass

mode

B2 If the UPS goes to the maintenance bypass mode, switch on the maintenance bypass switch, otherwise do the

maintenance in accordance with the process A;

B3 Remove the right panel, left panel and top cover, do the maintenance

B4 Install the right, left panels and top cover

B5 Switch on the input/output switch, the UPS enter the maintenance bypass mode

B6 Switch off the maintenance switch, install baffles and screws, the unit goes to the bypass mode;

B7 If both the mains and battery are normal, the unit goes into the line mode and charging after a period of time;

Troubleshooting

This chapter provides information that can help you to locate faults with the E90 UPS.

Some data may have to be measured to fix the fault. If it needs to be measured during the operation, the device

should be isolated from the mains. In this case, a transformer can be used between device and the power. It also

applies to the bypass input.

Warning: when UPS works, a large amount of energy is stored in the internal BUS capacitor, it cannot be guaranteed that there is no electricity inside the UPS with mains isolation, so it needs extra attention when maintenance. Disconnect all external input power of the fault machine for maintenance. After opening the case, use the bleed resistor to release the energy stored in BUS capacitor to avoid injury to person.

Before maintenance, please confirm the related reliable cable connection.

For the UPS fault, please record the software version and PCB version correctly.

Warning s and precautions:

When fault occurs, make a note of the display (refer to code table) as the reference for maintenance.

Note: the UPS mains input switch cannot be OFF arbitrarily to avoid electricity interruption.

Fault analysis:

Record the status of display, then fix the reason in accordance with the following questions.

1. The input supply is abnormal? (over/under voltage)

2. Load changes( capacity or type)

3. Fire

4. There’s odor

5. Abnormal noise

6. Bad environment (dust or moisture)

7. High temperature of UPS or ambient environment

Troubleshooting

Failure view:

Please ensure the safe conditions before starting the maintenance. Please read chapter 2 “Security conditions”

and chapter 3 “shutdown-disassembly/reassembly UPS”;

After remove the case, checking the following items:

1. The CONNECTOR or terminals loose

2. The transformer or other parts burst or discoloration especially the power components on the heat sink

3.Capacitor rupture or leak

4.Any parts serious blow up especially power components on heat sink

Solutions:

1. If the unit fails, due to higher probability damage of the INV-POWER board, replace the power board is ok.

2. If any power component on the power board is founded to blow up, replace it according to the “replace PCB”;

3. If fan doesn’t work with mains input, confirm that if the auxiliary power of the INV-POWER board is damaged

and needs to be replaced

4. Charger shows abnormal, check if the charging circuit in the PFC power board is damaged and need to be

replaced.

The display has no light and response when connected mains

No light and response for

Refer to chapter 2 and

chapter 3 for operation

Check if the ±15V in INV-

POWER board is normal

YES

NO

Check If the fuse of INV-

POWER board is good

NO	Replace the fuse

YES

Replace INV-power board

NO

If repaired

YES

END

Common fault troubleshooting

| LCD display fault code | UPS alarm | Buzz | LED | The board may be damaged(1 shows the max. Probability, 2 shows the less probability) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 3 |
| 1 | Rectifier fault | long beep | Fault ON | PFC power board | PFC inductor board | control detec- tion board |
| 2 | Inv. fault(include Inv. Bridge arm ) | long beep | Fault ON | INV power board | INV inductor board | control detec- tion board |
| 3 | Inv. SCR short | long beep | Fault ON | INV inductor board | control detec- tion board |  |
| 4 | Inv. SCR break | long beep | Fault ON | INV inductor board | control detec- tion board |  |
| 5 | Bypass SCR short | long beep | Fault ON | PFC inductor board | control detec- tion board |  |
| 6 | Bypass SCR break | long beep | Fault ON | PFC inductor board | control detec- tion board |  |
| 7 | Fuse broken | long beep | Fault ON | INV inductor board |  |  |
| 8 | Paralle Relay fault | long beep | Fault ON | control detec- tion board |  |  |
| 9 | Fan fault | long beep | Fault ON | fan | INV power board |  |
| 10 | Reserve | long beep | Fault ON |  |  |  |
| 11 | Auxiliary power fault | long beep | Fault ON | INV power board | control detec- tion board |  |
| 12 | Power initializa- tion fault | long beep | Fault ON | control detec- tion board |  |  |
| 13 | Positive battery Charge fault | long beep | Fault ON | PFC power board | PFC inductor board | control detec- tion board |
| 14 | Negative battery Charge fault | long beep | Fault ON | PFC power board | PFC inductor board | control detec- tion board |
| 15 | Bus over-voltage | long beep | Fault ON | PFC power board | PFC inductor board | control detec- tion board |
| 16 | Bus under-volt- age | long beep | Fault ON | PFC power board | PFC inductor board | control detec- tion board |
| 17 | Large difference between ±Bus | long beep | Fault ON | PFC power board | PFC inductor board | control detec- tion board |
| 18 | Soft start fail | long beep | Fault ON | PFC power board | PFC inductor board | control detec- tion board |
| 19 | Rectifier over- temperature | twice/s | Fault ON | PFC power board | fan |  |
| 20 | Inv. Over-tem- perature | twice/s | Fault ON | INV power board | fan |  |

| LCD display fault code | UPS alarm | Buzz | LED | The board may be damaged(1 shows the max. Probability, 2 shows the less probability) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 3 |
| 21 | Input neutral loss | twice/s | Fault ON |  |  |  |
| 22 | Battery reverse | twice/s | Fault ON | connection wrong | control detec- tion board |  |
| 23 | Parallel connec- tion fault | twice/s | Fault ON | Parallel cable not connect- ed well | control detec- tion board |  |
| 24 | CAN communi- cation fault | twice/s | Fault ON | Setting paral- lel mode but only single UPS working | control detec- tion board |  |
| 25 | Share current when parallel fault | twice/s | Fault ON | Parallel cable problem | control detec- tion board |  |
| 26 | Battery high voltage | once/s | Fault flash | battery fault | PFC power board | control detec- tion board |
| 27 | Input phase se- quence reverse | once/s | Fault flash | connection wrong |  |  |
| 28 | Bypass reverse | once/s | Fault flash | connection wrong |  |  |
| 29 | Output short circuit | once/s | Fault flash | output short |  |  |
| 30 | Rectifier over- current | once/s | Fault flash | PFC power board | control detec- tion board |  |
| 31 | Bypass over- current | once/s | BPS flash | bypass out- put overload |  |  |
| 32 | Over load | once/s | INV or BPS flash | output over- load |  |  |
| 33 | No battery | once/s | BATTERY flash | battery dis- connected | battery volt- age abnormal |  |
| 34 | Battery voltage low | once/s | BATTERY flash | Low battery and shutdown |  |  |
| 35 | Low battery pre- alarm | once/s | BATTERY flash | Battery low and pre-alarm |  |  |
| 36 | Internal commu- nication error | once/2s | Fault flash | control detec- tion board |  |  |
| 37 | Inv. DC exces- sive | once/2s | INV flash | INV inductor board | control detec- tion board |  |
| 38 | Overload in parallel | once/2s | INV flash | output over- load | Redundancy number set- ting is im- proper | control detec- tion board |

| LCD display fault code | UPS alarm | Buzz | LED | The board may be damaged(1 shows the max. Probability, 2 shows the less probability) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 3 |
| 39 | Mains voltage abnormal | once/2s | BATTERY ON | Input voltage abnormal |  |  |
| 40 | Mains frequency abnormal | once/2s | BATTERY ON | Input fre- quency abnormal |  |  |
| 41 | Bypass ultra protection |  | BPS flash | bypass abnor- mal |  |  |
| 42 | Bypass ultra tracking |  | BPS flash | bypass abnor- mal |  |  |
| 43 | Start invalid |  |  | Inverter can- not be started due to some faults |  |  |
| 44 | Reserve |  |  |  |  |  |
| 45 | Inverter not on |  |  | The inverter not start after 2min without any alarm |  |  |
| 46 | Output switch not ON | Once per 3s |  | Detect output switch | Output signal in the detec- tion board is wrong |  |

Battery replacement

1. Refer to the user’s manual for battery installation operation;

2. Ensure the safe conditions before any operation. Please read chapter 2 ”Security conditions” and chapter 3

”shutdown-disassembly/reassembly UPS” carefully. Be careful when disconnecting the battery. Short circuit will

damage the battery or wiring.

Note:

The battery with the same brand/type/date of manufacture is recommended to ensure a long battery life. The

voltage difference among the batteries should not more than ±150 mV.

We recommended to measure the voltage of each battery during discharge to ensure the voltage differences no

more than ±150mV. The battery pack capacity will be affected if there is one or more battery voltages differ too

much. In the worst case, it will damage the other battery.

The voltage difference should be reduced after a long period of charging.

E90 standard battery string:

1. Switch of the battery switch (if have) , remove the battery baffle;

2. remove the battery, and use the new battery

3. carefully checked if all the connection is good

4. Re-install the battery drawer;

5. Measure the total voltage of the battery;

6. Install all screws, baffles, switch on the battery switch (if have).

Single Battery cabinet:

1. Close the battery switch(if have) ;

2. Disconnect the connection between the UPS and the battery cabinet;

3. Replace the battery according to the battery cabinet user’s manual;

4. Thoroughly check if all the connections are correct;

5. Measure the total voltage of the battery;

6. Open the battery switch(if have)

PCB replacement

Warning:when UPS works, a large amount of energy is stored in the internal BUS capacitor, it cannot be

guaranteed that there is no electricity inside the UPS with mains isolation, so it needs extra attention when

maintenance. Disconnect all external input power of the fault machine for maintenance. After opening the case,

use the bleed resistor to release the energy stored in BUS capacitor to avoid injury to person.

General instruction

The internal voltage of the UPS is high enough to cause serious personal injury or death.

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully. Be careful when disconnecting the battery. Short circuit will

damage the battery or wiring.

2. ESD(electrostatic discharge) precautions: The PCB is very sensitive to electrostatic. When pick and place the

board, ensure that the operating personnel and equipment are grounded well.

The new board is taken out from the anti-static packaging only when necessary, the old board removed from the

UPS should be immediately placed in anti-static packaging.

3. Shut down the UPS according to the process A or B in chapter 3.

4. When disconnect any connectors, hold the male while pulling the female (sometimes need to press the connector snaps) , otherwise, it will make the connector or PCB bending.

Mark it before disconnecting in order to facilitate the re-assembly connector.

5. Ensure the compatibility between the new board and old board before replacement.

6. When re-install the connector, the male and female should be aligned, or the PCB or UPS will be damaged.

7. Confirm if the connection is correct after replacing PCB.

Input EMI board replacement

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully.

2. Operate according to the steps 1-3 of process A or steps 1-3 of process B in chapter 3;

3. Remove the screws of left panel of UPS, remove the cover, use the bleeder resistor to release the energy

stored in the Bus capacitor;

4. Remove all the cables of the EMI board;

5. Remove all the screws of the EMI board;

6.  Replace the PCB, package the old PCB;

7. Install the screws and cables;

8. install the right panel and screws ;

9. Continue with the steps 4-9 in process A or 4-8 in process B in chapter 3;

Replace DSP board

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully.

2. Operate according to the steps 1-3 of process A or steps 1-3 of process B in chapter 3;

3. Remove the screws of left panel of UPS, remove the cover, use the bleeder resistor to release the energy stored

in the Bus capacitor;

4. Remove all the cables of the DSP board;

5. Remove all the screws of the DSP board;

6. Replace the PCB, package the old PCB;

7. Install the screws and cables;

8. install the right panel and screws;

9. Continue with the steps 4-9 in process A or 4-8 in process B in chapter 3;

Replace PFC inductor board

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully.

2. Operate according to the steps 1-3 of process A or steps 1-3 of process B in chapter 3;

3. Remove the screws of left panel of UPS, remove the cover, use the bleeder resistor to release the energy stored

in the Bus capacitor;

4. Remove all the cables of the PFC inductor board;

5. Remove all the nuts and screws of the PFC inductor board;

6. Replace the PCB, package the old PCB;

7. Install the nuts, screws and cables;

8. install the left panel and screws;

9. Continue with the steps 4-9 in process A or 4-8 in process B in chapter 3;

Replace PFC power board

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully.

2. Operate according to the steps 1-3 of process A or steps 1-3 of process B in chapter 3;

3. Remove the screws of left panel of UPS, remove the cover, use the bleeder resistor to release the energy stored

in the Bus capacitor;

4. Remove all the cables of the PFC power board

5. Remove all the screws of the PFC power board;

6. Replace the PCB, package the old PCB;

7. Install the screws and cables;

8. install the right panel and screws;

9. Continue with the steps 4-9 in process A or 4-8 in process B in chapter 3;

Replace INV inductor board

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully.

2. Operate according to the steps 1-3 of process A or steps 1-3 of process B in chapter 3;

3. Remove the screws of left panel of UPS, remove the cover, use the bleeder resistor to release the energy stored

in the Bus capacitor;

4. Remove all the cables of the INV inductor board

5. Remove all the screws and nuts of the INV inductor board;

6. Replace the PCB, package the old PCB;

7. Install the nuts, screws and cables;

8. install the left panel and screws;

9. Continue with the steps 4-9 in process A or 4-8 in process B in chapter 3;

Replace INV power board

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully.

2. Operate according to the steps 1-3 of process A or steps 1-3 of process B in chapter 3;

3. Remove the screws of left panel of UPS, remove the cover, use the bleeder resistor to release the energy

stored in the Bus capacitor;

4. Remove all the cables of the INV-POWER board

5. Remove all the screws of the INV power board;

6. Replace the PCB, package the old PCB;

7. Install the screws and cables;

8. install the right panel and screws;

9. Continue with the steps 4-9 in process A or 4-8 in process B in chapter 3;

LCD on front panel

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully.

2. Operate according to the steps 1-3 of process A or steps 1-3 of process B in chapter 3;

3. Open the front panel, remove 4pcs of nuts of the rear panel and then remove the rear panel;

4. Remove all the cables of the PCB

5. Remove all the screws of the PCB;

6. Replace the PCB, package the old PCB;

7. Install the screws and cables;

8. Install the rear panel and nuts;

9. Continue with the steps 4-9 in process A or 4-8 in process B in chapter 3;

Replace fan

(2 fans are provided)

1. Ensure the safe conditions before any operation. Please read chapter 2 “Security conditions” and chapter 3

“shutdown-disassembly/reassembly UPS” carefully.

2. Operate according to the steps 1-3 of process A or steps 1-3 of process B in chapter 3;

3. Remove the screws of right and left panels, remove the cover, use the bleeder resistor to release the energy

stored in the Bus capacitor;

4. Remove the fan cables of the INV power board;

5. Remove all the screws of the fan;

6. Replace with a new fan;

7. Install the screws and cables;

8. Install right and left panels, and the screws;

9. Continue with the steps 4-9 in process A or 4-8 in process B in chapter 3;

PCB static maintenance

PFC inductor board

| NO. | Description | Type | Checked compo- nents | Detect Pin | Meter stall | Normal | abnormal |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | AC rectify | Diode | D1, D3, D6, D11, D14, D16 | A/K | diode | 0.36V | open or short |
| 2 | mains input | Relay | K1,K2,K6 | 4/5 | Ω | open | short |
| 3 | Battery input | SCR | D7, D9, D18, D19, D20, D21 | A/K | Ω | open | Short |
| 4 | Battery input | SCR | D7, D9, D18, D19, D20, D21 | G/K | Ω | ≈10Ω | open or short |
| 5 | Charge | SCR | Q70, Q71 | A/K | Ω | open | Short |
| 6 | Charge | SCR | QJ1, QJ4, QJ5, QJ6, QJ7, QJ8, QJ3,QJ12 | G/K |  |  |  |
| 7 | Bypass | SCR | QJ1, QJ4 ,QJ5,QJ6, QJ7,QJ8 ,QJ3,QJ12 | A/K | A/K | open | Short |
| 8 | Bypass | SCR | K7,K8,K9 | G/K | G/K | ≈10Ω | open or short |
| 9 | Bypass | Relay | K3, K4, K5 | 1/3 | 1/3 | open | short |

PFC power board

| NO. | Description | Type | Checked compo- nents | Detect Pin | Meter stall | Normal | abnormal |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | BOOST | Diode | D7-D12 | A/K | diode | 0.36V | open or short |
| 2 | BOOST | IGBT | Q1-12 | E->C | diode | ≈0.4V | open or short |
| 3 | BOOST | IGBT | Q1-12 | G/E | Ω | ≈10KΩ | open or short |
| 4 | Charge | FUSE | F3-4 |  | Ω | 0Ω | open |
| 5 | Charge | MOS- FET | Q13-14 | S->D | diode | ≈0.46V | open or short |
| 6 | Charge | MOS- FET | Q13-14 | G/S | Ω | ≈20KΩ | open or short |

INV inductor board

| NO. | Description | Type | Checked compo- nents | Detect Pin | Meter stall | Normal | abnormal |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | INV | FUSE | F1-3 |  | Ω | 0Ω | open |
| 2 | INV | SCR | SCR1-6 | A/K | Ω | Open | Short |
| 3 | INV | SCR | SCR1-6 | G/K | Ω | 20~40Ω | open or short |
| 4 | INV | Relay | RLY1-3 | 1/3 | Ω | open | short |

INV power board

| NO. | Description | Type | Checked compo- nents | Detect Pin | Meter stall | Normal | abnormal |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | INV | IGBT | Q1-12 | E->C | diode | ≈0.4V | open or short |
| 2 | INV | IGBT | Q1-12 | G/E | Ω | ≈10KΩ | open or short |
| 3 | Auxiliary power | FUSE | F1 |  | Ω | 0Ω | open |
| 4 | Auxiliary power | MOS- FET | Q14-15 | S->D | diode | ≈0.46V | open or short |
| 5 | Auxiliary power | MOS- FET | Q14-15 | G/S | Ω | ≈10KΩ | open or short |

Stand-alone commissioning

Warning: When UPS is working, the internal Bus capacitor stores a lot of energy. But isolated with mains cannot

guarantee completely no electricity inside the UPS and need extra attention when do the maintenance. When

cut off all the external input power supplied for maintenance, use the bleed resistor to release the energy stored

in Bus capacitor after open the case firstly to avoid causing injury to persons.

Please refer to the “UPS repair/maintenance”, especially the “Security maintenance conditions” and “ Close-

Disassembly/Reassembly UPS”.

The stand-alone commissioning requires intact UPS.

Startup steps

1) Before startup, confirm that the input/output connection is correct; measure the positive and negative battery

voltage, battery breaker is temporarily open.

2) Close the UPS Output switch.

3) Close the UPS input switch. Close external input mains and start UPS by AC.

4) After AC start, check the LCD menu, working mode, matching ID number, the VA of UPS, output voltage

level and the frequency is the same with the actual values.( refer to the following pictures). If not the same,

immediately disconnect the mains to check or cal the customer service hotline.

Main Page: default display

The main data page is shown below. The display can be changed to view other data or information,

view or change settings, or view records. Press the scroll key to highlight the other choices on the right

side of the screen and press the enter key to enter the highlighted page.

Data : Press the scroll key for approximately 1 sec. to highlight Data.  The Data page will display all

three phases of input and output voltage, current, and frequency and output load percentage as shown

below.

While in the Data page, additional data pages to view will be shown on the right side of the screen. Input: Press ENTER key for approximately 1 sec. The display will show all three phases of the Main

voltage, current, and frequency and the Bypass voltage and frequency as shown below.

Output: Press the scroll key for approximately 1 sec. The display will show all three phases of the

Output voltage, current, and frequency as shown below.

Battery: Press scroll key for approximately 1 sec. The display will show the Battery voltage, current, estimated battery runtime and battery capacity as shown below.

Load : Press the scroll key for approximately 1 sec. The display will show all three phases of the Load %, kW, and kVA  as shown below

INSIDE: press	key for approximately 1 sec. to move to the fifth page, the fifth page of data is Inside

data.

Inside: Press the scroll key for approximately 1 sec.  The display will show the internal V-BUS (DC bus voltage), T1/T2 (Temperature 1 and Temperature 2), V-Inv (Inverter Voltage), and F-Inv (Inverter Frequency) as shown below.

Info: Press the scroll key for approximately 3 sec. to exit Data, and press the scroll key for approximately

1 sec. move to Info.   The display will show LCD, PFC, and INV software versions and power rating as

shown below.

Setting: Press the scroll key for approximately 1 sec. to move to the setting page, then press ENTER key to enter setting-user page. Press the scroll key to change item, press ENTER key to enter item and press the scroll key to change value, press ENTER key confirm the setting.

Available settings are:

| Setting | Values | Default |
| --- | --- | --- |
| Language: | English, Portuguese, Italian, Deutsch, Polish, Spanish, or French | English |
| Backlight: | On, 10 – 100s in 10s increments | ON |
| Buzzer: | Enable or Disable | Enable |
| Test Now: | OFF, 10s, 10m, EOD -End Of Discharge | OFF |

Test Now: Press ENTER key to enter test now item, press the scroll key to select test value and press ENTER to confirm. The Battery manual test command can test battery discharge for 10s, 10min and to EOD.

Maintenance : Press	+ ENTER  key to enter maintenance and display a password window, press change the number and press ENTER to select the value, the password is “1121”.

Record : Displays event records and fault records. Displays the Index (number in list), Time of event or fault, State (Mode) of UPS and event or fault as shown in the examples below.

Record-Event : Press the scroll key to select Up or Down or Delete. Press ENTER key to confirm. Record-Fault : Press the scroll key to select Up or Down or Delete. Press ENTER key to confirm. Note: If Delete is selected, all event or fault records will be deleted.

Maintenance: All system parameter setting are controlled by two keys, Scroll and Enter. Scroll - Moves through the parameters and adjusts values

Enter – Goes into setting pages and confirms values.

To enter the Maintenance  - System parameter setting mode, press the Scroll and Enter keys simultaneously for 3 seconds. The display will show a password window, press the Scroll key to change the number and press Enter to select the value, the password is “1121”.

Once the Maintenance password is entered, press the Enter key. The UPS goes into the Setting-System window as shown below.

Setting-System: press the Enter key to enter item and confirm value, press the Scroll key to change the value.

The following parameters can be adjusted:

| Setting-System | Range | Default |
| --- | --- | --- |
| Working Mode | Normal, Parallel, ECO | ECO1 |
| V Output Grade2 | 120 or 127 | 120 |
| F Output Grade3 | 50 or 60 | 60 |
| F mode | CVCF or Non-CVCF | Non-CVCF |
| Test type | OFF, 10s, 10min or EOD | Off |
| Test Cycle | 1~30 days | 30 days |
| Equipment ID4 | 1 - 15 | 1 |
| Temp. Sensor SW | ON or OFF5 | Off |

1) Factory default setting for Working Mode is ECO. To disable ECO, reprogram Working Mode to Normal or

Parallel.

2)  Must be in static bypass to change

3) If not in static bypass, output will drop load

4) This is the MODBUS device address used for RS232 & RS485 communication ports.

a. Press Scroll key to set the address.

b. When battery temperature sensor is open, choose ID 1~10 & 13~15

c. If UPS is set for parallel mode and device address <= parallel quantity, device address = parallel ID

d. Press “ON” to exit the device address setting and save the device address setting value and parallel ID setting.

e. Note: Under single UPS mode, until this device address setting save and exit, single UPS setting is done.

5) OFF turns off the sensor switch, ON turns on the sensor switch and send query command to sensor with

address 11 and 12 every second.

Press the Scroll key to highlight Bypass and press the Enter key to enter the Setting-Bypass window as shown

below.

Setting-Bypass: press the Enter key to enter item and confirm value, press the Scroll key to change the value.

The following parameters can be adjusted:

| Setting-Bypass | Range | Default |
| --- | --- | --- |
| Upper Limit | 10%, 15%, 20%, 25% | 25% VAC |
| Lower Limit | -10%, -20%, -30%, -40% | -40% VAC |
| F_Range | 1%, 2%, 4%, 5%, 10% | 10% HZ |

Press the Scroll key to highlight Battery and press the Enter key to enter the Setting-Battery window as shown

below.

Setting-Battery: press the Enter key to enter item and confirm value, press the Scroll key to change the value.

The following parameters can be adjusted:

| Setting-Battery | Range | Default |
| --- | --- | --- |
| Number1 | 20 | 20 |
| Capacity2 | 7 - 2000 | 9AH |
| Boost Charge | Enable or disable | Enable |
| Group3 | 1-19 | 1 |
| V-Boost | 2.30-2.40, step is 0.01V | 2.30 vpc |
| V-Float | 2.20-2.29, step is 0.01V | 2.27 vpc |
| V-EOD | 1.60-1.90V | 1.67 vpc |
| I-Maxcharge4 | 1-20A | Capacity x Group x .15 |

1. Number is the number of batteries per string

2. Capacity is the Amp-Hour rating of the batteries per string

3. Group is the number of strings of batteries

4. I-Maxcharge is the maximum charger current. Setting this above 15A on the E90-10kVA increases the input

current rating and requires an input circuit for 45A

Press the Scroll key to highlight Parallel and press the Enter key to enter the Setting-Parallel window as shown

below.

Setting-Parallel: press the Enter key to enter item and confirm value, press the Scroll key to change the value.

The following parameters can be adjusted:

| Setting-Parallel | Range | Default |
| --- | --- | --- |
| ID1 | 1-4 | 1 |
| Number2 | 1-4 | 1 |
| Redu. Num3 | 1-3 | 0 |

1. ID - Program each UPS in Parallel with a unique ID

2. Number - Program the total number of UPS systems in parallel. Maximum of 4 in parallel.

3. Redu. Num. – Program to the total number of UPS systems in parallel to be used for redundancy

Parallel system commissioning

Warning: When UPS is working, the internal Bus capacitor stores a lot of energy. But isolated with mains cannot

guarantee completely no electricity inside the UPS and need extra attention when do the maintenance. When

cut off all the external input power supplied for maintenance, use the bleed resistor to release the energy stored

in Bus capacitor after open the case firstly to avoid causing injury to persons.

Please refer to the “UPS repair/maintenance”, especially the “Security maintenance conditions” and “ Close-

Disassembly/Reassembly UPS”.

Parallel system should be commissioning when the stand-alone are all intact.

Parallel system should be commissioning when the stand-alone are all intact.

Take 4 units in parallel for example.

1) Confirm the input/output wires connection and input phase sequence are correct; switch off the battery

breaker, and measure the +/- bat voltage of all battery group are normal.

2) Connect the parallel cable, it should be formed loop connection

3) Switch on the input breaker of unit 1,and access LCD setting interface to setting the working mode ID parallel

number redundant number. Require setting the in series number capacity of battery. The output voltage level

and Bypass protection range are default setting.

4) Turn off the input breaker of Unit 1, and make sure the UPS is off. Turn on the input breaker of Unit 2,access

the LCD setting interface, setting the parallel working mode, ID NO.2, parallel 4 units, redundant number .The

other setting are the same as UPS 1 operation.

5) For Unit 3 and Unit 4 UPS, the operation setting are all the same as Unit 1 and 2.

6) Turn on Bypass/input/output breaker of all the paralleled UPS, then confirm all the setting are correct. Each

UPS has their owed different ID.

7) Turn on all the battery breaker and confirm the parameter (V/I) are normal.

8) Connected the Load, and check whether the output current are balance.

Switch on and off the utility breaker to test all the UPS converters system from Utility to battery and restored

function are working find

Shutdown steps

1) Confirm the load information to avoid overload when turn off single unit;

2) Shut down each UPS according to the stand-alone UPS shutdown steps.

Emergency shutdown

Connect all the EPO ports to a key switch according to the following figure. When emergency occurs, switch on

the key can turn off all the outputs of UPS in this parallel system.

Software upgrade

There are two methods for software upgrade.

Use C2000 emulator to upgrade

When shutdown the UPS, remove the right panel of UPS, burn the DSP in control detection board

separately to upgrade. For detailed steps, please refer to the C2000 simulator instruction.

Use RS232 port to realize online upgrade

Remove the panel of the maintenance breaker, turn on the breaker so that the UPS goes to

maintenance bypass mode.

Turn on the UPS with utility. Open the serial program software Prg2800_33.exe

Note:

a) When burning is finished, the other DSP cannot be burned until the DSP buzz. ( after burning INV,

about 5S later, the next burning can be performed. When finish burning the REC, the next burning can

be executed after about 20s).

b) If it fails during the REC burning, it will show “ Program was

unsuccessful”.  Switch off the UPS and then restart, click “Update” to re-burn.

c) If it fails during the INV burning, it will show “Program was

unsuccessful”. Switch off the UPS and then restart, modify the ID number to 1 in the software. Close the

serial port and then open it, click “Re-Update” to start the re-burning.

d) During the burning, it repeats a frame data which goes into

an infinite loop. Restart the UPS and Prg2800_33 and check if the communication connection is ok.

Then re-burn can be operated. If it is the REC burning, please refer to the item b, if INV burning, please

refer to item c.

e) If the REC and INV burning are both fail, the INV burning

(Re-Update) has to be operated firstly. Cut off the mains and then power on the UPS, then the REC

burning (Update) can be executed.

Follow the settings in Figure (1)

“1” is to choose serial port that the computer uses;

“2” choose speed 9600;

“3” choose RS232;

“4” is to choose the ID number for the UPS that we are programmed. For single unit, it’s ID1, for parallel unit, it’s

the same as the ID number as we set in the UPS LCD.

“5” for laptop, pls set the value ≥5; for desktop computer, can set the value <5;

“6” choose 07;

“7” choose INV for the program, because we are going to update the inverter program; the same is REC program.

“8” is default value, no need to change;

“10”is for the target software “INV33.out”that we are going to program. pls note that you have to click “11” to

choose target upgrade file

After the setting done, pls click “Open device” as shown in Fig (1)

e time, you can only use one of them at one time.

Figure(1)

After the above steps, it shows below Fig (2), pls click the “OK” button

Figure(2)

Connect the UPS RS232 to the computer’s serial port, make sure the communication between them is good

Figure(3)

After set up the communication between UPS and computer, click “Update” as shown in Figure (4)

Figure(4)

Figure (5) shows the chip is preparing for the program

Figure(5)

Figure (6) shows the program work is proceeding

Follow below Figs 7/8/9 to finish and exit.

Figure(6)

If need go on the programming, pls return to step 3.

If finish and stop the programming, pls turn OFF the maintenance breaker, put on the panel, work the

UPS to inverter power supply.

Figure(7)

Figure(8)

Figure(9)

Appendix A: UPS fault judgment

| No. | UPS Alarm | Software judgment |  |  |  | Buzz | LED |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Condition 1 | Condition 2 | Condition 3 | Condition 4 |  |  |
| 1 | Rectifier fault | DC BUS over- voltage | DC BUS under- voltage | Large bus difference |  | long beep | Fault ON |
| 2 | Inv. fault(include Inv. Bridge arm ) | The absolute value of the output voltage >112.5% of rated output voltage, last 500ms |  | Bridge arm midpoint voltage( Inv. voltage) last 500ms >1.1 time of rat- ed peak value 360vfor230 344for220 376for240 |  | long beep | Fault ON |
| 3 | Inv. SCR short |  |  |  |  | long beep | Fault ON |
| 4 | Inv. SCR break | (in parallel, X phase load rate<6.3%) &&(parallel X phase total load rate>50%) &&(large loop current¦¦in bypass mode) last time 2S |  |  |  | long beep | Fault ON |
| 5 | Bypass SCR short | (X phase Output voltage>60% of rated) &&(the absolute values of other phases voltage<5% of rated voltage) last 2s |  |  |  | long beep | Fault ON |
| 6 | Bypass SCR break | ((in parallel, X phase load rate <6.3%) &&(parallel X phase total load rate<50%) &&(large loop current¦¦ in Bypass mode) ) ¦¦(X phase cur- rent>10% of rated&&X phase Output voltage>50% of the Bypass voltage) last 2S |  |  |  | long beep | Fault ON |
| 7 | Fuse broken | Hardware signal low available |  |  |  | long beep | Fault ON |
| 8 | Parallel Relay fault | ( Inv. status&&Relay open) ¦¦(no Inv. Status && parallel Relay close) last 20ms |  |  |  | long beep | Fault ON |
| 9 | Fan fault | Hardware signal low available for 5s |  |  |  | long beep | Fault ON |
| 10 | Reserve |  |  |  |  | long beep | Fault ON |
| 11 | Auxiliary power fault | Hardware signal low available for 3ms |  |  |  | long beep | Fault ON |
| 12 | Power initializa- tion fault | 1) Rec.DSP read IIC self-test, until 15s power on) Inv. DSP read IIC self- test, until 15s delay unit not obtain valid parameter from E2PROM, jumper error, jumper type is not defined, DSP internal RAM self-test error(MCU cannot completely modify RAM) |  |  |  | long beep | Fault ON |
| 13 | Positive bat- tery Charge fault |  |  |  |  | long beep | Fault ON |
| 14 | Negative bat- tery Charge fault |  |  |  |  | long beep | Fault ON |
| 15 | Bus over-volt- age | +bus voltage>470V Last time: 20ms | -bus voltage >470V Last time: 20ms |  |  | long beep | Fault ON |
| 16 | Bus under- voltage | Bus volt- age <280V time:120ms | Bus voltage is 10V lower than setting value Time: 2min |  |  | long beep | Fault ON |

| No. | UPS Alarm | Software judgment |  |  |  | Buzz | LED |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Condition 1 | Condition 2 | Condition 3 | Condition 4 |  |  |
| 17 | Large differ- ence between ±Bus | 30V difference between ±bus |  |  |  | long beep | Fault ON |
| 18 | Soft start fail | 10s later, soft start bus volt- age is lower than 300V | During the soft start, ±bus voltage <1.2 times of in- put voltage for 120ms |  |  | long beep | Fault ON |
| 19 | Rectifier over- temperature | Last 0.2s>77°C show PFC over temperature |  |  |  | twice/s | Fault ON |
| 20 | Inv. Over-tem- perature | Last 0.2s>77°C show inverter over tempera- ture |  |  |  | twice/s | Fault ON |
| 21 | Input neutral loss |  |  |  |  | twice/s | Fault ON |
| 22 | Battery reverse | +battery volt- age< -50V | -battery volt- age >+50V |  |  | twice/s | Fault ON |
| 23 | Parallel con- nection fault | Parallel cable fault under the parallel : 10ms |  |  |  | twice/s | Fault ON |
| 24 | CAN communi- cation fault | Parallel number more than 1 for single unit and powered UPS is no more than 1 unit |  |  |  | twice/s | Fault ON |
| 25 | Share current when parallel fault |  |  |  |  | twice/s | Fault ON |
| 26 | Battery high voltage | Setting Charge voltage +20V |  |  |  | once/s | Fault flash |
| 27 | Input phase sequence reverse | Obtain by algorithm |  |  |  | once/s | Fault flash |
| 28 | Bypass reverse | Obtain by algorithm |  |  |  | once/s | Fault flash |
| 29 | Output short circuit | X phase Output voltage is lower than rated 30%&&X phase Out- put current is 70% of rated current |  |  |  | once/s | Fault flash |
| 30 | Rectifier over- current |  |  |  |  | once/s | Fault flash |
| 31 | Bypass over- current | X phase Bypass Output current greater than the rated 125% |  |  |  | once/s | BPS flash |
| 32 | Over load | X phase load rate( Inv. or Bypass) greater than rated 105% |  |  |  | once/s | INV or BPS flash |

| 33 | No battery | Battery voltage lower than 50V |  |  |  | once/s | BAT- TERY flash |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 34 | Battery voltage low | Battery voltage lower (EOD voltage*6*battery pcs) |  |  |  | once/s | BAT- TERY flash |
| 35 | Low battery pre-alarm | Battery EOD voltage+(battery pcs *6(SetJarNum) *1.5) |  |  |  | once/s | BAT- TERY flash |
| 36 | Internal com- munication error | Comm. Error between Recti- fier and Inv. |  |  | once/2s | Fault flash |  |
| 37 | Inv. DC exces- sive | DC component average value is more than 2V last 2S |  |  |  | once/2s | INV flash |
| 38 | Overload in parallel | X phase load rate is more than total load rate of parallel system: 400ms |  |  |  | once/2s | INV flash |
| 39 | Mains voltage abnormal | Higher than 270V | Lower than 182V |  |  | once/2s | BAT- TERY ON |
| 40 | Mains frequen- cy abnormal | Higher than 70Hz | Lower than 38Hz |  |  | once/2s | BAT- TERY ON |
| 41 | Bypass ultra protection | Bypass power down and not available |  |  |  |  | BPS flash |
| 42 | Bypass ultra tracking | Bypass abnormal but powered, and bypass instantaneous nor- mal, then change the Bypass to ultra tracking |  |  |  |  | BPS flash |
| 43 | Start invalid | 1) rectifier not start completely or start fault a) over-tempera- ture b) fan fault c) SCR fault and shutdown d) bridge arm short and shutdown e) power board fault f) software fail g) battery re- verse and shutdown h) user operation fault(maint. Bypass close) i) Auxiliary power power down and shutdown 2) manually start invalid |  |  |  |  |  |
| 44 | Reserve |  |  |  |  |  |  |
| 45 | Inverter not on |  |  |  |  |  |  |
| 46 | Output switch not ON |  |  |  |  | Once per 3 seconds |  |