M90 Modbus Protocol

www.xpcc.com | © 2022 Xtreme Power Conversion Corporation. All rights reserved. (Rev 6/3/22)

Protocol in M90

1.	Warning item	2

2. Capability setting（look for Application example 1）	3

3. Support Capability list	4

4. Control item（look for Application example 2）	5

5. The result of control	6

6. Setting Parameter to default value	7

7. UPS working status	7

8. UPS  battery information (sys or rack info inquiry addr)	7

9.The temperature inquiry	8

10. The three phase load inquiry	8

11. The bypass three phase info	8

12. The output power factor inquiry	8

13. Load level inquiry	9

14. UPS working Mode	9

15. UPS fault information	9

16. Output Socket	9

17. Loss point	9

18. Setting Parameter item	10

19. Setting Parameter succeed or fail	10

20. Remote shutdown and test	10

21. CPU information	10

22. UPS model and rating information	11

23. The parller inquiry	11

24.Date inquiry  (sys or rack info inquiry addr)	11

25.Set date  (sys or rack info set addr)	12

26.On line module ID number inquiry and select	12

Note	12

1. Note1	12

2. Note2	13

3. Note3	13

4. Note4	14

Application example	15

1. Audible alarm Enable or Disable	15

2. Setting buzzer beeps Silent.	15

3. Setting control parameter to default value	15

4. Get input voltage	16

5. Output socket status	16

6. Remote shut down the UPS	16

7. Shut down UPS and auto restart later	16

8. Setting Parameter item	16

：unused

- Protocol in M90

- Warning item

| Hex | Dec | Size | Content | Bit value | type |
| --- | --- | --- | --- | --- | --- |
| 0x0000 | 0 | bit15 | bit15 = EPO is Active |  |  |
|  |  | bit14 | bit14 = Load is over load level and reach countdown delay |  |  |
|  |  | bit13 | bit13= CAN bus is abnormal | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | bit12= Load level is over Overload Alarm Level | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | bit11= Battery is not connected. (Battery voltage is less than 9V) | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | bit10 = Battery is over 15V |  |  |
|  |  | bit9 | bit9 = Module is not locked |  |  |
|  |  | bit8 | bit8 = Including: EPO is active, Maintain Bypass is active, DC start, But DC start setting is disable Line Status is not OK. (Voltage or Frequency is out of range, Phase sequence is not correct, Neutral Loss) SYNCHRO signal is abnormal TRIG0 signal is abnormal |  |  |
|  |  | bit7 | bit7 = Charger is abnormal |  |  |
|  |  | bit6 | bit6 = Checksum value of Eeprom Data saved in MCU is not correct |  |  |
|  |  | bit5 | bit5 = Fan Locked |  |  |
|  |  | bit4 | bit4 = Line Phase sequence is not correct |  |  |
|  |  | bit3 | bit3 = Bypass Phase sequence is not correct |  |  |
|  |  | bit2 | bit2 = Neutral is absent |  |  |
|  |  | bit1 | bit1 = Initial communication between DSP & MCU is abnormal |  |  |
|  |  | bit0 | bit0 = SYNCHRO signal is abnormal |  |  |
| 0x0001 | 1 | bit15 | bit15 = TRIG0 signal is abnormal |  |  |
|  |  | bit14 | bit14 = Power Module number is not consistent with setting |  |  |
|  |  | bit13 | bit13 = No STS in system |  |  |
|  |  | bit12 | bit12 = Maintain Bypass is active |  |  |
|  |  | Bit11 | Bit11 = |  |  |
|  |  |  | bit10- bit0 = Reservation |  |  |
| 0x0002 | 2 | bit15 | bit15-bit7 = Reservation |  |  |
|  |  | bit6 | bit6 = Reservation |  |  |
|  |  | bit5 | bit5 = Reservation |  |  |
|  |  | bit4 | bit4 = Reservation |  |  |
|  |  | bit3 | bit3 = Reservation |  | R |
|  |  | bit2 | bit2=Alarm:P1 cut off pre-alarm | 0:FALSE/1:TRUE | Read only |
|  |  | bit1 | bit1 = Reservation |  |  |
|  |  | bit0 | bit0=Alarm:Battery open | 0:FALSE/1:TRUE | Read only |
| 0x0003 | 3 | bit15 | bit15 = Reservation |  |  |
|  |  | bit14 | bit14=Alarm:IP site fail | 0:FALSE/1:TRUE | Read only |
|  |  | bit13 | bit13=Alarm:Battery over charge | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | bit12=Alarm:Overload warning | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | bit11=Alarm:Fan lock warning | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | bit10=Alarm:EPO active | 0:FALSE/1:TRUE | Read only |
|  |  | bit9 | bit9 = Reservation |  |  |
|  |  | bit8 | bit8=Alarm:Over temperature | 0:FALSE/1:TRUE | Read only |
|  |  | Bit7 | bit7-bit0 = Reservation |  |  |

- 2. Capability setting（look for Application example 1）

| Hex | Dec | Size | Content | Bit value | Register value | type |
| --- | --- | --- | --- | --- | --- | --- |
| 0x00 0E | 14 | bit15 | bit15=Enable/disable audible alarm | 0:FALSE/1:TRUE | E:8000/D:7FFF | Read/Write |
|  |  | bit14 | bit14=Enable/disable battery mode audible warning | 0:FALSE/1:TRUE | E:4000/D:BFFF | Read/Write |
|  |  | bit13 | bit13=Enable/disable battery open status check | 0:FALSE/1:TRUE | E:2000/D:DFFF | Read/Write |
|  |  | bit12 | bit12=Enable/disable Site fault detect | 0:FALSE/1:TRUE | E:1000/D:EFFF | Read/Write |
|  |  | bit11 | bit11=Set hot standby master/slave, PEM means master, PD | 0:FALSE/1:TRUE | E:800/D:F7FF | Read/Write |
|  |  | bit10 | bit10=Enable/disable auto-Restart. | 0:FALSE/1:TRUE | E:400/D:FBFF | Read/Write |
|  |  | bit9 | bit9=Enable/disable battery deep discharge protect | 0:FALSE/1:TRUE | E:200/D:FDFF | Read/Write |
|  |  | bit8 | bit8=Enable/disable battery low protect | 0:FALSE/1:TRUE | E:100/D:FEFF | Read/Write |
|  |  | bit7 | bit7=Enable/disable code start | 0:FALSE/1:TRUE | E:80/D:FF7F | Read/Write |
|  |  | bit6 | bit6=Enable/disable bypass forbidding | 0:FALSE/1:TRUE | E:40/D:FFBF | Read/Write |
|  |  | bit5 | bit5=Enable/disable short restart 3 times | 0:FALSE/1:TRUE | E:20/D:FFDF | Read/Write |
|  |  | bit4 | bit4=Enable/disable inverter short clear function | 0:FALSE/1:TRUE | E:10/D:FFEF | Read/Write |
|  |  | bit3 | bit3=Enable/disable bypass when device turn off. | 0:FALSE/1:TRUE | E:8/D:FFF7 | Read/Write |
|  |  | bit2 | bit2=Enable/disable bypass audible warning | 0:FALSE/1:TRUE | E:4/D:FFFB | Read/Write |
|  |  | bit1 | bit1=Enable/disable high efficiency mode | 0:FALSE/1:TRUE | E:2/D:FFFD | Read/Write |
|  |  | bit0 | bit0=Enable/disable energy saving |  | E:1/D:FFFE | Read/Write |
| 0x000F | 15 | bit15 | bit15=Enable/disable Output socket1 when the delay release | 0:FALSE/1:TRUE | E:8000/D:7FFF | Read/Write |
|  |  | bit14 | bit14=Enable/disable Output socket2 when the delay release | 0:FALSE/1:TRUE | E:4000/D:BFFF | Read/Write |
|  |  | bit13 | bit13=Enable/disable deep high efficiency mode | 0:FALSE/1:TRUE | E:2000/D:DFFF | Read/Write |
|  |  | bit12 | bit12=Enable/disable converter mode | 0:FALSE/1:TRUE | E:1000/D:EFFF | Read/Write |
|  |  |  | Bit11-bit10 = Reservation |  |  |  |
| 0x000F | 15 |  |  |  |  |  |
|  |  | Bit7 | Bit7 = Enable/disable period self test Z | 0:FALSE/1:TRUE | E:80/D:FF7F | Read/Write |
|  |  | Bit6 | Bit6 = Enable/disable limited runtime on battery mode, | 0:FALSE/1:TRUE | E:40/D:FFBF | Read/Write |
|  |  |  | bit0 - b11 =Reservation |  |  |  |

- 3. Support Capability list

| Hex | Dec | Size | Content | Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0010 | 16 | bit15 | Support: Enable/disable audible alarm | 0:FALSE/1:TRUE | Read Only |
|  |  | bit14 | Support: Enable/disable battery mode audible warning | 0:FALSE/1:TRUE | Read Only |
|  |  | bit13 | Support: Enable/disable battery open status check | 0:FALSE/1:TRUE | Read Only |
|  |  | bit12 | Support: Enable/disable Site fault detect | 0:FALSE/1:TRUE | Read Only |
|  |  | bit11 | Support: Set hot standby master/slave, PEM means master, PD | 0:FALSE/1:TRUE | Read Only |
|  |  | bit10 | Support: Enable/disable auto-Restart. | 0:FALSE/1:TRUE | Read Only |
|  |  | bit9 | Support: Enable/disable battery deep discharge protect | 0:FALSE/1:TRUE | Read Only |
|  |  | bit8 | Support: Enable/disable battery low protect | 0:FALSE/1:TRUE | Read Only |
|  |  | bit7 | Support: Enable/disable code start | 0:FALSE/1:TRUE | Read Only |
|  |  | bit6 | Support: Enable/disable bypass forbidding | 0:FALSE/1:TRUE | Read Only |
|  |  | bit5 | Support: Enable/disable short restart 3 times | 0:FALSE/1:TRUE | Read Only |
|  |  | bit4 | Support: Enable/disable inverter short clear function | 0:FALSE/1:TRUE | Read Only |
|  |  | bit3 | Support: Enable/disable bypass when device turn off. | 0:FALSE/1:TRUE | Read Only |
|  |  | bit2 | Support: Enable/disable bypass audible warning | 0:FALSE/1:TRUE | Read Only |
|  |  | bit1 | Support: Enable/disable high efficiency mode | 0:FALSE/1:TRUE | Read Only |
|  |  | bit0 | Support: Enable/disable energy saving | 0:FALSE/1:TRUE | Read Only |
| 0x0011 | 17 | bit15 | Support: Enable/disable Output socket1 when the delay release | 0:FALSE/1:TRUE | Read Only |
|  |  | bit14 | Support: Enable/disable Output socket2 when the delay release | 0:FALSE/1:TRUE | Read Only |
|  |  | bit13 | Support: Enable/disable deep high efficiency mode | 0:FALSE/1:TRUE | Read Only |
|  |  | bit12 | Support: Enable/disable converter mode | 0:FALSE/1:TRUE | Read Only |
|  |  |  | bit0 - bit11 =Reservation |  |  |
|  |  | Bit7 | Bit7 = Enable/disable period self test Z | 0:FALSE/1:TRUE | Read Only |
|  |  | Bit6 | Bit6 = Enable/disable limited runtime on battery mode, | 0:FALSE/1:TRUE | Read Only |

- 4. Control item（look for Application example 2）

| Hex | Dec | Size | Content | Bit value | Register value | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0x001A | 26 | bit15 | bit15=Silence buzzer beep | 0:FALSE/1:TRUE | Y:8000/N:7FFF | Read/Write |
|  |  | bit14 | bit14=buzzer beep open | 0:FALSE/1:TRUE | Y:4000/N:BFFF | Read/Write |
|  |  | bit13 | bit13=Test until battery low | 0:FALSE/1:TRUE | Y:2000/N:DFFF | Read/Write |
|  |  | bit12 | bit12=Remote turn off UPS | 0:FALSE/1:TRUE | Y:1000/N:EFFF | Read/Write |
|  |  | bit11 | bit11=Remote turn on UPS | 0:FALSE/1:TRUE | Y:800/N:F7FF | Read/Write |
|  |  | bit10 | bit10=Cancel shutdown | 0:FALSE/1:TRUE | Y:400/N:FBFF | Read/Write |
|  |  | bit9 | bit9=Cancel test | 0:FALSE/1:TRUE | Y:200/N:FDFF | Read/Write |
|  |  | bit8 | bit8=10 seconds test | 0:FALSE/1:TRUE | Y:100/N:FEFF | Read/Write |
|  |  | bit7 | bit7= Reservation |  |  |  |
|  |  | bit6 | bit6 = Reservation |  |  |  |
|  |  | bit5 | bit5= Reservation |  |  |  |
|  |  | bit4 | bit4 = Reservation |  |  |  |
|  |  |  | b3-b0 = Reservation |  |  |  |
| 0x001B | 27 |  | b15-b11 = Reservation |  |  |  |
|  |  | Bit10 | UPS turn to bypass | 0:FALSE/1:TRUE | Y:0400/N:FFFB | Read/Write |
| 0x0422 | 1058 | Bit15 | EPO function open | 0:FALSE/1:TRUE | Y:8000/N:7FFF | Read/Write |
|  |  | Bit14 | EPO function close | 0:FALSE/1:TRUE | Y:4000/N:BFFF | Read/Write |
|  |  | Bit13 | modeoutputfrequency 50Hz | 0:FALSE/1:TRUE | Y:2000/N:DFFF | Read/Write |
|  |  | Bit12 | mode output frequency 60Hz | 0:FALSE/1:TRUE | Y:1000/N:EFFF | Read/Write |
|  |  | Bit11 | charger On | 0:FALSE/1:TRUE | Y:0800/N:F7FF | Read/Write |
|  |  | Bit10 | charger Off | 0:FALSE/1:TRUE | Y:0400/N:FBFF | Read/Write |
|  |  | Bit9 | Enable independent battery | 0:FALSE/1:TRUE | Y:0200/N:F7FF | Read/Write |
|  |  | Bit8 | Disable independent battery | 0:FALSE/1:TRUE | Y:0100/N:FBFF | Read/Write |
|  |  | Bit7 | Select rack1 | 0:FALSE/1:TRUE | Y:0080/N:F7FF | Read/Write |
|  |  | Bit6 | Select rack2 | 0:FALSE/1:TRUE | Y:00400/N:FBFF | Read/Write |

- 5. The result of control

| Hex | Dec | Size | Content | Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0025 | 37 | bit15 | bit15=Flag:Silence buzzer beep | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit14 | bit14=Flag:buzzer beep open | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit13 | bit13=Flag:Test until battery low | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit12 | bit12=Flag:Remote turn off UPS | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit11 | bit11=Flag:Remote turn on UPS | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit10 | bit10=Flag:Cancel shutdown | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit9 | bit9=Flag:Cancel test | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit8 | bit8=Flag:10 seconds test | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit7 | bit7= Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit6 | bit6 = Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit5 | bit5= Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit4 | bit4 = Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  |  | b3-b0 = Reservation | 0:FAIL/2:SUCCESS | Read/Write |
| Hex | Dec | Size | Content | Bit value | Type |
| 0x0026 | 38 |  | b15-b12 = Reservation | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | Bit10 | Bit10 = UPS turn to bypass | 0:FAIL/1:SUCCESS | Read/Write |
|  |  |  | B9-b0 = Reservation | 0:FAIL/2:SUCCESS | Read/Write |
| 0x0423 | 1059 | Bit15 | EPO function in normal open | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | Bit14 | EPO function in normal close. | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | Bit13 | mode output frequency 50 | 0:FAIL/1:SUCCESS | Read only |
|  |  | Bit12 | mode output frequency 60 | 0:FAIL/1:SUCCESS | Read only |
|  |  | Bit11 | charger On | 0:FAIL/1:SUCCESS | Read only |
|  |  | Bit10 | charger Off | 0:FAIL/1:SUCCESS | Read only |
|  |  | Bit9 | Enable independent battery | 0:FAIL/1:SUCCESS | Read only |
|  |  | Bit8 | Disable independent battery | 0:FAIL/1:SUCCESS | Read only |
|  |  | Bit7 | Select rack1 | 0:FAIL/1:SUCCESS | Read only |
|  |  | Bit6 | Select rack2 | 0:FAIL/1:SUCCESS | Read only |

- 6. Setting Parameter to default value

| Hex | Dec | Size | Content | Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0030 | 48 | bit15 | bit15=Seting control parameter to default value | 0:FAIL/1:SUCCESS | Read/Write |
|  |  |  | b14-b0 = Reservation |  |  |
| 0x003B | 59 | bit15 | bit15=Flag:Seting control parameter to default value | 0:FAIL/1:SUCCESS | Read |
|  |  |  | b14-b0 = Reservation |  |  |

- 7. UPS working status

| Hex | Dec | Size | Content | units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x031E | 798 | 1 | R Input voltage | 0.1V | ReadOnly |
| 0x031F | 799 | 1 | S Input voltage | 0.1V | ReadOnly |
| 0x0320 | 800 | 1 | T Input voltage | 0.1V | ReadOnly |
| 0x0321 | 801 | 1 | Input frequency | 0.1Hz | ReadOnly |
| 0x0322 | 802 | 1 | R Output voltage | 0.1V | ReadOnly |
| 0x0323 | 803 | 1 | S Output voltage | 0.1V | ReadOnly |
| 0x0324 | 804 | 1 | T Output voltage | 0.1V | ReadOnly |
| 0x0325 | 805 | 1 | Output frequency | 0.1Hz | ReadOnly |
| 0x0326 | 806 | 1 | R Output current | 0.1A | ReadOnly |
| 0x0327 | 807 | 1 | S Output current | 0.1A | ReadOnly |
| 0x0328 | 808 | 1 | T Output current | 0.1A | ReadOnly |
| 0x0329 | 809 | 1 | R Output load percent | 1% | ReadOnly |
| 0x032A | 810 | 1 | S Output load percent | 1% | ReadOnly |
| 0x032B | 811 | 1 | T Output load percent | 1% | ReadOnly |
| 0x032C | 812 | 1 | P Battery voltage | 0.1V | ReadOnly |
| 0x032D | 813 | 1 | N Battery voltage | 0.1V | ReadOnly |
| 0x032E | 814 | 1 | Max Temperature of the detecting pointers | 0.1C | ReadOnly |
| 0x032F | 815 | 1 | Note1 | Note1 | ReadOnly |

- 8. UPS  battery information (sys or rack info inquiry addr)

| 0x00BC | 188 | 1 | P Battery voltage | 0.1V | ReadOnly |
| --- | --- | --- | --- | --- | --- |
| 0x00BD | 189 | 1 | P Battery piece number |  | Read/write |
| 0x00BE | 190 | 1 | P Battery nominal capacity(Ah) | Ah | Read/Write |
| 0x00BF | 191 | 1 | P Battery capacity | % | ReadOnly |
| 0x00C0 | 192 | 1 | P Battery remain time | minutes | ReadOnly |
| 0x00C1 | 193 | 1 | N Battery voltage | 0.1V | ReadOnly |
| 0x00C2 | 194 | 1 | N Battery piece number |  | ReadOnly |
| 0x00C3 | 195 | 1 | N Battery nominal capacity(Ah) | Ah | Read/Write |
| 0x00C4 | 196 | 1 | N Battery capacity | % | ReadOnly |
| 0x00C5 | 197 | 1 | N Battery remain time | minutes | ReadOnly |
| 0x0318 | 792 | 1 | P Battery charge current | 0.01A | ReadOnly |
| 0x0319 | 793 | 1 | N Battery charge current | 0.01A | ReadOnly |
| 0x0307 | 775 | 1 | The battery Total AH information Inquiry | AH | ReadOnly |
| 0x0308 | 776 | 1 | EPO status QREPO | 8000：open/ 7FFF：close | ReadOnly |

- 9.The temperature inquiry

| 0x00CC | 204 | 1 | temperature1 | ℃ | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x00CD | 205 | 1 | Temperature2 | ℃ | Read only |
| 0x00CE | 206 | 1 | Temperature3 | ℃ | Read only |
| 0x00CF | 207 | 1 | Temperature4 | ℃ | Read only |

- 10. The three phase load inquiry

| 0x00DD | 221 | 1 | R phase of load | 0.1% | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x00FC | 252 | 1 | S phase of load | 0.1% | Read only |
| 0x00FD | 253 | 1 | T phase of load | 0.1% | Read only |
| 0x00FE | 254 | 1 | The whole load | 0.1% | Read only |

- 11. The bypass three phase info

| 0x011A | 282 | 1 | R voltage of bypass | 0.1V | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x011B | 283 | 1 | S voltage of bypass | 0.1V | Read only |
| 0x011C | 284 | 1 | T voltage of bypass | 0.1V | Read only |
| 0x011D | 285 | 1 | R current of bypass | 0.1A | Read only |
| 0x011E | 286 | 1 | S current of bypass | 0.1A | Read only |
| 0x011F | 287 | 1 | T current of bypass | 0.1A | Read only |
| 0x0123 | 291 | 1 | frequency of bypass | 0.1Hz | Read only |

- 12. The output power factor inquiry

| 0x030F | 783 | 1 | R output power factor |  | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x0310 | 784 | 1 | S output power factor |  | Read only |
| 0x0311 | 785 | 1 | T output power factor |  | Read only |

- 13. Load level inquiry

| 0x0312 | 786 | 1 | R Watt percent | % | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x0313 | 787 | 1 | S Watt percent | % | Read only |
| 0x0314 | 788 | 1 | T Watt percent | % | Read only |
| 0x0315 | 789 | 1 | R VA percent | % | Read only |
| 0x0316 | 790 | 1 | S VA percent | % | Read only |
| 0x0317 | 791 | 1 | T VA percent | % | Read only |

- 14. UPS working Mode

| 0x00D0 | 208 | 1 | UPS Mode inquiry | Note2 | ReadOnly |
| --- | --- | --- | --- | --- | --- |

- 15. UPS fault information

| 0x02A3 | 675 | 1 | Fault kind ASC | Note3 | ReadOnly |
| --- | --- | --- | --- | --- | --- |
| 0x02A4 | 676 | 1 | Battery voltage before fault | 0.1V | ReadOnly |
| 0x02A5 | 677 | 1 | I/P frequency before fault | 0.1Hz | ReadOnly |
| 0x02A6 | 678 | 1 | I/P voltage before fault | 0.1V | ReadOnly |
| 0x02A7 | 679 | 1 | Inverter O/P frequency before fault | 0.1Hz | ReadOnly |
| 0x02A8 | 680 | 1 | Inverter O/P voltage before fault | 0.1V | ReadOnly |
| 0x02A9 | 681 | 1 | Negative Bus voltage before fault | 0.1V | ReadOnly |
| 0x02AA | 682 | 1 | Positive Bus voltage before fault | 0.1A | ReadOnly |
| 0x02AB | 683 | 1 | O/P load before fault | 0.1V | ReadOnly |
| 0x02AC | 684 | 1 | O/P current before fault | 0.1V | ReadOnly |
| 0x02AD | 685 | 1 | Temperature before fault | 0.1℃ | ReadOnly |
| 0x02AE | 686 | 1 | UPS running status before fault | Note4 | ReadOnly |

- 16. Output Socket

| Hex | Dec | Size | Content | Bit value/ units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0346 | 838 | Bit15 | b0=Output socket 1 status inquiry | 0:OFF / 1:ON | ReadOnly |
|  |  | bit14 | b1=Output socket 2 status inquiry | 0:OFF / 1:ON | ReadOnly |
|  |  |  | b13-b0 = Reservation |  |  |
| 0x038B | 907 | 1 | Output socket release1 delay time inquiry in battery mode | minutes | Read/Write |

- 17. Loss point

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x034A | 842 | 1 | High efficiency modeVoltage high loss point | V | Read |
| 0x034B | 843 | 1 | High efficiency modeVoltage low loss point | V | Read |
| 0x034C | 844 | 1 | Free run mode frequency high loss point | Hz | Read |
| 0x034D | 845 | 1 | Free run mode frequency low loss point | Hz | Read |
| 0x034E | 846 | 1 | The bypass Freq high loss point | 0.1Hz | Read |
| 0x034F | 847 | 1 | The bypass Freq low loss point | 0.1Hz | Read |
| 0x0350 | 848 | 1 | The bypass Voltage high loss point | V | Read |
| 0x0351 | 849 | 1 | The bypass Voltage low loss point | V | Read |

- 18. Setting Parameter item

| 0x02ED | 749 | 1 | Setting the battery shut down delay time | second | Read/Write |
| --- | --- | --- | --- | --- | --- |
| 0x02EE | 750 | 1 | Battery Cut-off minimum voltage per cell | 0.01V | Read |
| 0x02EF | 751 | 1 | Cut off voltage per PCS（！！！） BATCO(10.00~11.00) | 0.01V | Read/Write |
| 0x02f0 | 752 | 1 | Battery low voltage per PCS | 0.01V | Read/Write |
| 0x02f1 | 753 | 1 | Battery low capacity(%) | % | Read/Write |
| 0x02f2 | 754 | 1 | Battery shutdown capacity(%) | % | Read/Write |
| 0x02f3 | 755 | 1 | The Period of period Self test Inquiry | Day | Read/Write |
| 0x0309 | 777 | 1 | Bat test stop time | S | ReadOnly |
| 0x030A | 778 | 1 | Bat test stop capacity | % | ReadOnly |
| 0x030B | 779 | 1 | Bat test stop voltage | 0.01V/PCS | ReadOnly |
| 0x034A | 842 | 1 | High efficiency mode Voltage high loss point | V | Read |
| 0x034B | 843 | 1 | High efficiency mode Voltage low loss point | V | Read |
| 0x034E | 846 | 1 | The bypass Freq high loss point | 0.1Hz | Read |
| 0x034F | 847 | 1 | The bypass Freq low loss point（1 2 or 4） | 0.1Hz | Read/Write |
| 0x0350 | 848 | 1 | The bypass Voltage high loss point 10 20 30 | V ；write：10 20 30 | Read/Write |
| 0x0351 | 849 | 1 | The bypass Voltage low loss point 10 20 30 | V ；write：10 20 30 | Read/Write |
| 0x0424 | 1060 | 1 | Setting battery Total AH | AH | Write |
| 0x05ED | 1457 | 1 | Setting Charging current | 02 to 64. | Read/Write |

- 19. Setting Parameter succeed or fail

| Hex | Dec | Size | Content | Bit value | type |
| --- | --- | --- | --- | --- | --- |
| 0x0384 | 900 | Bit15 | The Period of period Self test Inquiry | 0:FALSE/1:TRUE | Read only |
|  |  | Bit14 | Battery Cut-off minimum voltage per cell | 0:FALSE/1:TRUE | Read only |
|  |  | Bit13 | Battery low voltage per PCS | 0:FALSE/1:TRUE | Read only |
|  |  | Bit12 | Battery low capacity(%) | 0:FALSE/1:TRUE | Read only |
|  |  | Bit11 | Battery shutdown capacity(%) | 0:FALSE/1:TRUE | Read only |
|  |  | Bit10 | Bat test stop voltage | 0:FALSE/1:TRUE | Read only |
|  |  | Bit9 | Bat test stop capacity | 0:FALSE/1:TRUE | Read only |
|  |  | Bit8 | Bat test stop time | 0:FALSE/1:TRUE | Read only |
|  |  | Bit7 | Setting the battery shut down delay time | 0:FALSE/1:TRUE | Read only |
| 0x0385 | 901 | bit15 | Flag: High efficiency mode Voltage high loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | Flag: High efficiency mode Voltage low loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit13 | Flag: Reservation | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | Flag: Reservation | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | Flag: The bypass Freq high loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | Flag: The bypass Freq low loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit9 | Flag: The bypass Voltage high loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit8 | Flag: The bypass Voltage low loss point | 0:FALSE/1:TRUE | Read only |
|  |  |  | bit7-bit0 = Reservation |  |  |
|  | 1517 | Bit14 | Setting Charging current | 0:FALSE/1:TRUE | Read only |

- 20. Remote shutdown and test

| Hex | Dec | Size | Content | Units/Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x03AB | 939 | 1 | Shutdown | minutes(ASCII) | Read/Write |
| 0x03AC | 940 | 1 | Test for specified time | minutes(ASCII) | Read/Write |
| 0x03AD | 941 | 1 | Shutdown and restore(N) | minutes(ASCII) | Read/Write |
| 0x03AE | 942 | 2 | Shutdown and restore(M) | minutes(ASCII) | Read/Write |
| 0x03DA | 986 | bit15 | B15=flag:Shutdown | 0:FAIL/1:SUCCESS | Read only |
|  |  | bit14 | B14=flag:Test for specified time | 0:FAIL/1:SUCCESS | Read only |
|  |  | bit13 | B13=flag:Shutdown and restore | 0:FAIL/1:SUCCESS | Read only |
|  |  |  | b12-b0=Reservation |  |  |
| 0x030F | 783 | 1 | Get shutdown time | Unit: second | Read only |
| 0x0310 | 784 | 2 | Get Restore time | Unit: second | Read only |

- 21. CPU information

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x03E0 | 992 | 1 | Protocol ID Inquiry | ASCII | Read only |
| 0x03E1 | 993 | 10 | Main CPU Firmware version | ASCII | Read only |

- 22. UPS model and rating information

| 0x03EB | 1003 | 7 | Main Production type | ASCII | Read only |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Sub Production type | ASCII | Read only |
|  |  |  | VA type | ASCII | Read only |
|  |  |  | H/LV type | ASCII | Read only |
|  |  |  | Year | ASCII | Read only |
|  |  |  | Month | ASCII | Read only |
|  |  |  | Manufacturer ID | ASCII | Read only |
|  |  |  | Serial number | ASCII | Read only |
| 0x03F2 | 1010 | 1 | Battery Piece Number |  | Read only |
| 0x03F3 | 1011 | 1 | Battery standard voltage per unit | 0.1V | Read only |
| 0x03F4 | 1012 | 1 | Input phase |  | Read only |
| 0x03F5 | 1013 | 1 | Output phase |  | Read only |
| 0x03F6 | 1014 | 1 | Nominal I/P Voltage | V | Read only |
| 0x03F7 | 1015 | 1 | Nominal O/P Voltage | V | Read only |
| 0x03F8 | 1016 | 1 | Output power factor |  | Read only |
| 0x03F9 | 1017 | 2 | Output rated VA | W | Read only |
| 0x03FB | 1019 | 8 | Device model | ASCII | Read only |
| 0x048A | 1162 | 1 | Battery Voltage | 0.1V | Read only |
| 0x048B | 1163 | 1 | Rating Output Current | 0.1A | Read only |
| 0x048C | 1164 | 1 | Rating Output Frequency | 0.1Hz | Read only |
| 0x048D | 1165 | 1 | Rating Output Voltage | 0.1V | Read only |
| 0x048E | 1166 | 1 | The parallel number. |  | Read only |
| 0x031A | 794 | 1 | The setting redundant number |  | Read only |

- 23. The parller inquiry

| 0x02F4 | 756 | 1 | The paraller setting ASCII | 01:enable;00:disable | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x02F5 | 757 | 1 | The independent battery setting ASCII | 01:enable;00:disable | Read only |

- 24.Date inquiry  (sys or rack info inquiry addr)

| 0x03F3 | 759 | 2 | BatMaintenYear | ASC | Read only |
| --- | --- | --- | --- | --- | --- |
| 0x03F4 | 761 | 1 | BatMaintenMonth | ASC | Read only |
| 0x03F5 | 762 | 1 | BatMaintenDay | ASC | Read only |
| 0x03F6 | 763 | 2 | BatInstalYear | ASC | Read only |
| 0x03F7 | 765 | 1 | BatInstalMonth | ASC | Read only |
| 0x03F8 | 766 | 1 | BatInstalDay | ASC | Read only |
| 0x03F9 | 767 | 2 | SysMaintenYear | ASC | Read only |
| 0x03FB | 769 | 1 | SysMaintenMonth | ASC | Read only |
| 0x048A | 770 | 1 | SysMaintenDay | ASC | Read only |
| 0x048B | 771 | 2 | SysInstalYear | ASC | Read only |
| 0x048C | 773 | 1 | SysInstalMonth | ASC | Read only |
| 0x048D | 774 | 1 | SysInstalDay | ASC | Read only |

- 25.Set date  (sys or rack info set addr)

| 0x03F3 | 1061 | 4 | Set SysInstalDate | ASC | Write only |
| --- | --- | --- | --- | --- | --- |
| 0x03F4 | 1065 | 4 | Set SysMaintenDate | ASC | Write only |
| 0x03F5 | 1069 | 4 | Set BatInstalDate | ASC | Write only |
| 0x03F6 | 1073 | 4 | Set BatMaintenDate | ASC | Write only |

- 26.On line module ID number inquiry and select

| 0x02F6 | 758 | 1 | One module inquiry over flag | 0：over/other： fause | Read/Write |
| --- | --- | --- | --- | --- | --- |
| 0x0330 | 816 | 1 | Select on line module ID number | 0xFFFF：sys Defau: 0xFFFF | Read/Write |
| 0x0331 | 817 | 16 | On line module ID number inquiry |  | Read only |

- Note

# 1. Note1

| Note 1: |  |
| --- | --- |
| 815（bit15-bit8） | B8b9 00: standy; bit15 bit14 01: line-interactive; 10: on-line. |
|  | b7: Utility Fail b6: Battery Low b5: Bypass/Boost Active b4: UPS Failed b3: EPO b2: Test in Progress |
| 815 （bit3-bit0） | b1: Shutdown Active b0: bat silence a1: Bat test fail a0: Bat test OK |

# 2. Note2

| Note 2: |  |  |
| --- | --- | --- |
| 0x00D0H | P: | Power on mode |
|  | S: | Standby mode |
|  | Y: | Bypass mode |
|  | L: | Line mode |
|  | B: | Battery mode |
|  | T: | Battery test mode |
|  | F: | Fault mode |
|  | E: | HE/ECO mode |
|  | C: | Converter mode |
|  | D: | Shutdown mode |

# 3. Note3

| Code(FF) | Name | Definition |
| --- | --- | --- |
| 01 | cBusOver | BUS Voltage is over 450V |
| 02 | cBusUnder | BUS Voltage is under 320V, 200 ms |
| 03 | cBusUnbalance | +BUS, -BUS difference is over 50V, 200 ms |
| 04 | cBusShort | Hardware Signal Trigged |
| 06 | cBusSoftTimeOut | BUS softstart time is over 120 sec |
| 07 | cInvSoftTimeOut | Inverter Softstart time is over 120 sec |
| 08 | cInvVoltHigh | Inverter RMS is over 250V, 200ms |
| 09 | cInvVoltLow | Inverter RMS is under 150V, 200 ms |
| 10 | cRInvVoltShort | R phase Voltage is less 70V & Current is over 50A |
| 11 | cSInvVoltShort | S phase Voltage is less 70V & Current is over 50A |
| 12 | cTInvVoltShort | T phase Voltage is less 70V & Current is over 50A |
| 13 | cRSInvVoltShort | RS phase Voltage is less 70V & Current is over 50A |
| 14 | cSTInvVoltShort | ST phase Voltage is less 70V & Current is over 50A |
| 15 | cTRInvVoltShort | TR phase Voltage is less 70V & Current is over 50A |
| 16 | cInvRNegPow | 800Watt, 40ms; 400Watt, 100ms |
| 17 | cInvSNegPow | 800Watt, 40ms; 400Watt, 100ms |
| 18 | cInvTNegPow | 800Watt, 40ms; 400Watt, 100ms |
| 19 | cOverLoadFault | Overload happened, but bypass is not good |
| 20 | cBatteryFault | Battery is connected reversely |
| 22 | cOverTemperature | The max. temperature sensor is over 80 degree C |
| 25 | cCanFault | CAN bus is abnormal and Droop Source need to be changed |
| 26 | cSynSigFault | SYNCHRO Signal Fail |
| 27 | cTRIG0Fault | TRIG0 Signal |
| 28 | cRelayFault | Inverter Relay Short |
| 29 | cLineSCRFail | I/P SCR is Open |
| 31 | cSPSFault | SPS output is abnormal |
| 32 | cParaCableLoosenFault | Parallel Cable is lossen |
| 33 | cDSPMCUStopComm | DSP and MCU do not communicate |
| 34 | cBypassSCRFault | STS’s Bypass SCR is fail |
| 35 | cBypassTemperatureFault | STS is over temperature |
| 36 | cInvVoltOver | Inverter Sample voltage is over 380V, 156 us |

# 4. Note4

|  | Bit | Remarks |
| --- | --- | --- |
| 0x02AEH | 7 | 1:DCTODC on |
|  | 6 | 1:PFC on |
|  | 5 | 1: INVERTER on |
|  | 4 | Reserved(always 0) |
|  | 3 | 1:input relay on |
|  | 2 | 1:O/P relay on |
|  | 1 | Reserved(always 0) |
|  | 0 | Reserved(always 0) |

- Application example

- 1. Audible alarm Enable or Disable

Look for Enable audible alarm, It in table address 0x000E bit15.Then you may write 0x8000 to 0x000E to Enable audible alarm or write 0xEFFF to 0x0E to disable audible alarm.

For example:

[XX 10 00 0E 00 01 02 80 00 CRCL CRCH]Mean: Enable audible alarm.

[XX 10 00 0E 00 01 02 7F FF CRCL CRCH]Mean: Disable audible alarm.

Inquire the result of execute, you may read the follow address 0x10 bit15.

For example:

[XX 03 00 10 00 01 CRCL CRCH]

[XX 03 02 80 00 CRCL CRCH]Mean: Execute success

[XX 03 02 00 00 CRCL CRCH]Mean: Execute fail

- 2. Setting buzzer beeps Silent.

Look for silence buzzer beep in address 0x001A  bit 15 。Then you may write 0x8000 to 0x001A.

For example:

[XX 10 00 1A 00 01 02 80 00 CRCL CRCH]Silence buzzer beep.

Inquire the execution result. You may read 0x0025

[XX 03 00 25 00 01 CRCL CRCH] to inquire the results of command.

- 3. Setting control parameter to default value

Look for setting control parameter to default value it ,then write 0x8000 to 0x0030.If execute success then set 0x003B bit15 to 1;

For example:

[XX 10 00 30 00 01 02 80 00 CRCL CRCH]Setting control parameter to default value.

[XX 03 00 3B 00 01 CRCL CRCH]to inquire the results of command.

- 4. Get input voltage

Look for input voltage in address 0x00AA, when read 0x00AA to get input voltage and it units is 0.1V

For example:

PC:[XX 03 00 AA 00 01 CRCL CRH]

DEVICE:[XX 03 02 08 89 CRCL CRCH]

Mean: HEX [0x0889] to DEC[2185] .Input voltage:218.5V.

- 5. Output socket status

Inquire output socket status, Write socket number to 0x0345,then read 0x0346 to inquire socket status.

For example:

PC:[XX 10 03 45 00 01 02 01 00 CRCL CRCH] 01:Means inquire socket 1 status.

PC:[XX 03 03 46 00 01 CRCL CRCH]

DEVICE:[XX 03 02 01 00 CRCL CRCH]  01:Means socket1 was on.

- 6. Remote shut down the UPS

Remote shut down the UPS, then write is a number ranging from (.2, .3, ..., 01, 02,..., to 10)to the 0x3AB.If execute success then 0x003DA bit0 was set to 1.

For example:

PC:[XX 10 03 AB 00 01 02 2E 32]Mean: Shut down the UPS in 0.2 minutes

- 7. Shut down UPS and auto restart later

Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again. Then write n to 0x03AD and write m to 0x003AE.

For example:

PC:[XX 10 03 AD 00 03 06 2E 32 30 30 30 32 CRCL CRCH]Mean: Shut down the UPS in 0.2 minutes and waiting

for 0002 minutes turn on the UPS.

- 8. Setting Parameter item

Set The bypass Voltage high loss point of UPS ,You want to Set the value 286V . Then write 0x011E to 0x0350 .

For example:

PC:[XX 10 03 50 00 01 02 01 1E CRCL CRCH]Mean: Set The bypass Voltage high loss point of UPS for 286V.