## Slide 1
230 Yuma Street
Denver, CO 80223
(800) 582-4524
sales@xpcc.com
www.xpcc.com

## Slide 2
XPC TX90/T90 6kVA and 10kVA Training Agenda
  Features and Benefits
  Options
  Design and Operation
  Installation
  Front Panel
  System Operation
  Troubleshooting

## Slide 3
TX90 / T90 Features and Benefits
Online scalable UPS for high power and critical N+1 redundant applications
TX90 6kVA & 10kVA // Isolated Online Tower UPS 240/120VAC or 208/120VAC
T90 6kVA & 10kVA // Online Tower UPS 208VAC or 230VAC
Single module configurations: 6kVA/5.4kW and 10kVA/9kW
Parallel capacity configurations: 12kVA/10.8kW to 40kVA/36kW
Parallel redundant (N+1) configurations: 6kVA/5.4kW to 30kVA/27kW
UL, cUL, CE, FCC, RoHS
3 years electronics, 3 years battery warranty (USA)
Product snapshot
0.9 output power factor
Frequency converter
Parallel operation
Galvanic isolation transformer (TX90)
Hot swappable battery trays
Maintenance bypass
Extended battery runtimes
Lockable casters
Features

## Slide 4
TX90 / T90 Available Options
TX90 Standard Voltage: 208VAC input, 240 VAC Output
Voltages Available: 240V:240/120V, 230V:230/115V, 220V:220/110V, 200V:200/100V
  Factory Voltage Change Ordered as T9VCNFG
  Can be reconfigured in field
  208:208/120 Not used due to output phases being 120VAC + 88VAC
T90 Standard Voltage: 208 VAC Input, 208 VAC Output
  Optional voltages of 200/220/230/240VAC field selectable (firmware)
  No 120 Volt out
Voltage Options

## Slide 5
TX90 / T90 Available Options
Hardwired input and output standard
L6-30 Line Cord available for 6KVA
Configurable Output Receptacles Available
  I/O Box 1-5
XPD PDUs can provide additional outlets
I/O Configuration Options
I/O Box | Voltage | Recepts 1 | Recepts 2
I/O Box 1 | 240/120 | (2) C19 – 240V | (4) 5-15/20
I/O Box 2 | 120 | (2) C19 – 120V | (4) 5-15/20
I/O Box 3 | 240/120 | (2) L14-30 on 1 ft cord | (4) 5-15/20
I/O Box 4 | 240 | (2) L6-30 on 1 ft cord | (2) C19
I/O Box 5 | 208/120 | (2) C19 – 208V | (4) 5-15/20

## Slide 6
TX90 / T90 Available Options
TX90 and T90 Standard Internal Battery – 20 x 12V 9AH (10k) or 20 x 12V 7AH (6k) battery
  Located in hot swappable trays
Extended Internal Runtime Available for TX90 – 20 x 12V 580W battery
  Replaces standard battery
External Battery Cabinet Available – 20, 40, or 60 x 12V 9AH
  External cabinet can accommodate 1, 2 , or 3 strings
  Can be daisy chained for longer runtimes
  1000W External Battery Charger Available
Battery Options

## Slide 7
TX90 / T90 Available Options
SNMP Card
  SNMP-1PIN
Relay Dry Contact Interface Card
  TX90-Relay
  6 Output Relay Contacts
    Rated at 120VAC, 1A and 24VDC, 2A
  3 Input Contacts
Parallel Kit
  TX90-PK
  Communication cables to parallel systems
Communication Options

## Slide 8
Can Parallel up to 4 systems
Parallel for Capacity or Redundancy
  TX90-10k40 to TX90-40k40
  TX90-6k24 to TX90-24k24
Parallel Systems include:
  1-4 UPS systems with batteries
  Tie-Cabinet for output
    Includes System Bypass Breaker
  Parallel cable kit for communication
  Factory Startup – 5 x 8
Parallel Scalable Options
TX90 / T90 Available Options

## Slide 9
TX90 / T90 Available Options
Standard Warranty – 3 Year on Electronics and Battery
Extended 5 Year Warranty plans available on UPS and external battery
5 x 8 On-Site Service Plans
  3 Year plans for UPS and external battery
  5 Year plans for UPS and external battery
5 x 8 Startup available
  5 x 8 Startup included with parallel system packages
  7 x 24 Startup quoted by request
One time Preventative Maintenance available
Warranty and Service Options

## Slide 10
TX90 / T90 Design and Operation
TX90 One-Line
UPS Utility Input
UPS Utility Input Breaker
EMI Filter on UPS Utility Input
Rectifier and Booster
Internal Battery
Charger
Inverter
Auto Bypass Loop (Static Bypass)
UPS Output EMI Filter
Maintenance Bypass Switch
Output isolation transformer with adjustable input taps.

## Slide 11
TX90 / T90 Design and Operation
T90 One-Line

## Slide 12
TX90 / T90 Design and Operation
TX90 Rear Panel
A. RS-232 Port
B. Terminal Resistor for Parallel function
C. CAN Bus Connection Port for Parallel System
D. Optional Communication Slot 1
E. Optional Communication Slot 2
F. Cooling Fans
G. External Battery Connector
H. External Charger Connector
I. Utility Input Breaker CB1
K. CAM Switch (Maintenance Bypass Switch)
L. Input/Output Terminal Block (shown with cover removed)
M. Mounting Holes for External Charger Cabinet
N. EPO (Emergency Power Off): Short to enable the function
O. Thermal breaker for the protection of Load in abnormal
condition: CB3 (TX90-10K only)
P. Air Ventilation Hole

## Slide 13
TX90 / T90 Installation
Terminal Block Explanation
T90 Terminal Block – 208 or 240 Input and Output
  UPS Programming determines voltages
TX90 Terminal Block – 208 or 240 Input and 240/120 Output
  Transformer configuration and UPS programming determines voltages

## Slide 14
TX90 / T90 Installation
TX90 Transformer Windings
208 and 240 Volt Input Taps
  208 Default
  Can be Factory or Field Configured for 240
Dual Windings on Output
  Voltage Required determines Configuration

## Slide 15
TX90 / T90 Installation
TX90 Transformer Input Tap
208 Default
  UPS Programmed for 208V Inverter Output
240 Optional
  Reconfigure tap for 240V
  UPS Programmed for 240V Inverter Output
  Voltage change can be factory ordered

## Slide 16
TX90 / T90 Installation
TX90 Transformer Output Connections
240/120 VAC Default
  208/120 typically not recommended
  Jumpers are factory installed
120 VAC Full Capacity Optional
  Must reconfigure the jumpers

## Slide 17
TX90 / T90 Installation
Breaker and Wiring

## Slide 18
TX90 / T90 Installation
Parallel Tie Cabinet
Utilizes a GE Panelboard
UPS Output Breakers (UOB) for 4 Systems
Breakers are 40A for 6kVA or 60A for 10kVA
Main Breaker used as System Bypass Breaker (SSB)
Unused breaker locations can be used for System Output Breaker (SOB) or distribution breakers

## Slide 19
TX90 / T90 Installation
Parallel Installation

## Slide 20
TX90 / T90 Installation
Parallel Communications
Parallel communications set up as a token ring
Enable parallel operation
Each UPS programmed with a unique ID
Terminal Resistors of two end UPSs set to On

## Slide 21
TX90 / T90 Front Panel
Front Panel Includes:
LCD
LEDs
  S1 - Solid green LED - utility input voltage normal.
Flashing green LED - utility input voltage abnormal.
  S2 - Green LED indicates that Bypass Input is normal.
  N+1 - Green LED indicates that the UPS is able
to run under redundancy mode.
  ECO - UPS is working under ECO mode.
  UPS Fault or Abnormal
BUTTONS
  On - UPS ON/Alarm Silence
  Go to previous page or change the settings
  Enter - Confirm a changed setting.
  Go to the next page.
  Off - UPS OFF Switch
  Functions - Special functions log in/out

## Slide 22
TX90 / T90 Front Panel
Symbols on LCD

## Slide 23
TX90 / T90 Front Panel
Symbols on LCD

## Slide 24
TX90 / T90 System Operation
System Start Up
Verify Installation
  Clearances
  Environment
  Voltages
  Breaker and Wiring Sizes
  Connections
Verify that utility voltage and output voltage desired match UPS configuration
Verify that output breakers, if installed, are off
Turn on AC Input
UPS will go to bypass and start a self test
UPS is providing output power via static bypass and charging battery

## Slide 25
TX90 / T90 System Operation
System Start Up
Press the “ON” Button for 3 seconds
  UPS will beep twice and start another self test
  UPS will indicate test pass or fail
  If test pass, UPS will go into on line mode
  You can press the down arrow to step through displayed values

## Slide 26
TX90 / T90 System Operation
Viewing Monitored Values
  Press the down and up arrows to step through displayed values
  Bypass Input Voltage
  Utility Input Frequency
  Bypass Input Frequency
  Inverter Output Voltage
  Output Frequency
  % Load
  Battery Voltage
  UPS Internal Temperature

## Slide 27
TX90 / T90 System Operation
Viewing or Programming Function Settings
Press the “Function” Button to view settings
  Buzzer and Self-Test can be toggled by pressing Up Arrow
  Press Down Arrow to step to next function
Press ON and Down Arrow for 3 seconds to enter Function Programming Mode
  UPS must be in Off Mode to change functions other than Buzzer and Self-Test
  Function setting can be toggled to other settings by pressing Up Arrow
  Press Down Arrow to step to next function
  Press Enter Button at SAVE screen
  UPS will Lock and must be restarted
Functions
  Buzzer
    On or Off
  Self-Test
    On or Off

## Slide 28
TX90 / T90 System Operation
Viewing or Changing Function Settings
Bypass Voltage
  S_Lo - 184-260 VAC
  S_Hi - 195-260 VAC
Frequency Window
  ±3 Hz or ±1 Hz
Inverter Output Voltage
  200, 208, 220, 230, or 240 VAC
  Must be the same as Input Voltage
Operating Mode
  Normal, ECO, CF50, or CF60

## Slide 29
TX90 / T90 System Operation
Viewing or Changing Function Settings
Output Voltage Adjustment
  -1, -2, -3, 0, 1, 2, 3%
UPS Position in Parallel Mode
  Id01 through Id04
Parallel Function
  Po1 – Off
  Po2 - On
Save
  Press Enter
UPS is Locked
  Restart UPS

## Slide 30
TX90 / T90 System Trouble Shooting
Error Codes issued by UPS
Er01 1st stage DC BUS capacitor pre-charge abnormal after 50 seconds or Battery Fuse fails
Er02 AC SCR or Battery SCR soft Start abnormal after 2 seconds
Er03 3rd PFC(Boost) soft start abnormal after 30 seconds
Er04 Inverter out of order
Er05 Battery Weak or Dead
Er06 Output Short Circuit
EPO EPO Mode
Er08 DC Bus high-voltage-level abnormal
Er09 DC Bus low-voltage-level abnormal
Er10 Inverter Over-current
Er11 UPS Overheat
Er12 Inverter Overload

## Slide 31
TX90 / T90 System Trouble Shooting
Error Codes issued by UPS
Er13 Charger out of order or abnormal
Er14 Fan out of order
Er15 Wrong Procedure to Enter Maintenance Mode
Er16 Output Parameters Set Error in Parallel System
Er17 ID Numbers are in conflict in Parallel System or ID number Error in single unit
Er18 EEPROM’s data error. Its values are reset to default.
Er19 Reserved
Er20 DC Bus voltage can’t be discharged
Er21 Parallel communication error
(communication wire disconnected or failure to find ID1 UPS) in parallel system
Er22 Bypass SCR or Output Fuse Fails
Er23 Inverter Relay or SCR or Output Fuse Fails

## Slide 32
TX90 / T90 System Trouble Shooting
Error Codes issued by UPS
Er24 Bypass Input found when Running on CVCF mode
Er25 Reserved
Er26 PFC over-current
Er27 The UPS must be operated in normal mode in parallel system
Er28 Bypass Overload Time out and cut off output.
Er29 Charger Overcharges battery (>300Vdc)
Er30 Inverter Balance Error
Er31 The settings of both control board and driver board are not matched each other.
Er32 Sync Signal Error
Er33 Isolated transformer overheat
Er34 Balance function conflict

## Slide 33
TX90 / T90 System Trouble Shooting
Error Codes issued by UPS
CEr1 Utility voltage out of range
CEr2 Bypass Voltage out of range
CEr3 Inverter Voltage out of range
CEr4 Load Percentage out of range
CEr5 Battery Voltage out of range
CEr6 UPS Output Voltage out of range

## Slide 34
TX90 / T90 System Trouble Shooting
Special Remarks on Error Codes
When one of the Er06, EPO, Er23, Er24, Er28, Er32 ,or Er33 error message occurs, the UPS will have no output and lock itself immediately.
If the bypass voltage is normal(within specs), but one of the Er01, Er02, Er03, Er05, Er13, Er14, Er20, Er22, Er26, Er29 or Er30 error message occur, the UPS will transfer to Bypass loop and lock itself.
If the bypass voltage is normal(within specs), one of the Er04, Er08, Er09, Er10, Er11 or Er12 error message occurs, the UPS will transfer to Bypass loop, then try to transfer back to Inverter mode automatically. If the symptoms happen 4 times in one hour, the UPS will lock itself; otherwise, the error messages and the times of the error messages will be clear and reset automatically.
If the Er16, Er17, Er21, Er27, Er31 or Er34 error message occurs, the inverter of the UPS will have no output and the user is prohibited to turn on the UPS from the front panel.

## Slide 35
TX90 / T90 System Trouble Shooting
Trouble Shooting Error Codes
XPC TX90 6kVA & 10kVA Service Manual contains flow charts for each error code

## Slide 36
TX90 / T90 System Trouble Shooting
Trouble Shooting Error Codes

## Slide 37
TX90 / T90 System Trouble Shooting
PCB Locations
Control Board
Power Board
Fuse
Battery
DC Capacitor Board
Battery Charger Board
EPO
I/P EMI Filter Power
Cam Switch
O/P EMI Filter Board
Relay
Voltage Change Board

## Slide 38
Thank you, Questions?
Xtreme Power Conversion
230 Yuma Street
Denver, CO 80223
800.582.4524
Sales & Customer Support 1-800-582-4524 ext 1 sales@xpcc.com
Technical Support & Service 1-800-582-4524 ext 2 support@xpcc.com service@xpcc.com
Marketing marketing@xpcc.com