## Read Me
SNMP-2PG1 Modbus and BACnet map
Xtreme Power Conversion · SNMP-2PG1 (GENEREX CS141MINI-6, firmware 2.33.12)
Topic | Details
Applies to | Ai90, Li90, X90, E91, M90C and M90Ci UPS with the SNMP-2PG1 card. These UPS use the GENEREX default OEM map (confirmed by GENEREX, Oct 2026).
Source | GENEREX CS141 user manual v.2026-07-03, pages 286-288 (registers) and 346 (status bits); GENEREX BACnet UPS value table.
Enable | Modbus and BACnet are off by default. Enable them in the card web interface: Services > Setup, then Services > Modbus.
Modbus TCP port | 502 (fixed).
Addressing | Addresses are zero-based (0-65535). If your client counts from 1, add 1. Do not add a 4xxxx prefix.
Function codes | 03H (read holding registers) or 04H (read input registers); the card treats them the same.
Data type | 16-bit integer registers. U = unsigned, S = signed.
Status register | Register 109 / BACnet AI 12 is a bitmask; several bits can be set at once. See the Status Codes tab. Common values: 4 = normal, 5 = on bypass, 12 = on battery, 28 = on battery with battery low.
Alarms | Registers 115-138 / BACnet BI 0-23: 1 = active, 0 = not active.
Not in this map | Module count and status, redundancy, energy (kWh), output current and watts, and bypass values are available over SNMP only (MIB attached separately), where the UPS reports them.
Missing values | A value shown in the card web interface may have no Modbus register. Values the connected UPS does not report read as 0 or unsupported.

## Modbus Registers
Modbus registers
GENEREX default OEM map, as used by the SNMP-2PG1 on XPC UPS
Address (0-based) | Address (1-based) | Section | Name | Description and units | Type | Function
97 | 98 | UPS | OUTPUT_VOLT0 | Output Voltage Phase 1 in V | U | 3 / 4
98 | 99 | UPS | OUTPUT_VOLT1 | Output Voltage Phase 2 in V | U | 3 / 4
99 | 100 | UPS | OUTPUT_VOLT2 | Output Voltage Phase 3 in V | U | 3 / 4
100 | 101 | UPS | OUTPOWER0 | Outpower Phase 1 % | U | 3 / 4
101 | 102 | UPS | OUTPOWER1 | Outpower Phase 2 % | U | 3 / 4
102 | 103 | UPS | OUTPOWER2 | Outpower Phase 3 % | U | 3 / 4
103 | 104 | UPS | BATTCAP | Battery Capacity % | U | 3 / 4
104 | 105 | UPS | INVOLT0 | Input Voltage Phase 1 V | S | 3 / 4
105 | 106 | UPS | INVOLT1 | Input Voltage Phase 2 V | S | 3 / 4
106 | 107 | UPS | INVOLT2 | Input Voltage Phase 3 V | S | 3 / 4
107 | 108 | UPS | TEMPDEG | Temperature C° | S | 3 / 4
108 | 109 | UPS | AUTONOMTIME | Autonomy Time minutes | S | 3 / 4
109 | 110 | UPS | STATUS | UPS status bitmask; see Status Codes tab | U | 3 / 4
110 | 111 | UPS | BATTVOLT | Battery Voltage V | S | 3 / 4
111 | 112 | UPS | INFREQ0 | Input Frequency Hz Phase 1 | U | 3 / 4
112 | 113 | UPS | INFREQ1 | Input Frequency Hz Phase 2 | U | 3 / 4
113 | 114 | UPS | INFREQ2 | Input Frequency Hz Phase 3 | U | 3 / 4
114 | 115 | UPS | CNT_PF | Powerfail Counter | U | 3 / 4
115 | 116 | UPS | Alarm Battery Bad | 1 = active; 0 = not active | U | 3 / 4
116 | 117 | UPS | Alarm: On Battery | 1 = active; 0 = not active | U | 3 / 4
117 | 118 | UPS | Alarm: Battery Low | 1 = active; 0 = not active | U | 3 / 4
118 | 119 | UPS | Alarm: Battery Depleted | 1 = active; 0 = not active | U | 3 / 4
119 | 120 | UPS | Alarm: Over temperature | 1 = active; 0 = not active | U | 3 / 4
120 | 121 | UPS | Alarm: Input Bad | 1 = active; 0 = not active | U | 3 / 4
121 | 122 | UPS | Alarm: Output Bad | 1 = active; 0 = not active | U | 3 / 4
122 | 123 | UPS | Alarm: Output Overload | 1 = active; 0 = not active | U | 3 / 4
123 | 124 | UPS | Alarm: On Bypass | 1 = active; 0 = not active | U | 3 / 4
124 | 125 | UPS | Alarm: Bypass Bad | 1 = active; 0 = not active | U | 3 / 4
125 | 126 | UPS | Alarm: Output Off as requested. | 1 = active; 0 = not active | U | 3 / 4
126 | 127 | UPS | Alarm: UPS Off as requested. | 1 = active; 0 = not active | U | 3 / 4
127 | 128 | UPS | Alarm: Charger Failed | 1 = active; 0 = not active | U | 3 / 4
128 | 129 | UPS | Alarm: UPS Output Off | 1 = active; 0 = not active | U | 3 / 4
129 | 130 | UPS | Alarm: UPS System Off | 1 = active; 0 = not active | U | 3 / 4
130 | 131 | UPS | Alarm: Fan Failure | 1 = active; 0 = not active | U | 3 / 4
131 | 132 | UPS | Alarm: fuse failure | 1 = active; 0 = not active | U | 3 / 4
132 | 133 | UPS | Alarm: general fault | 1 = active; 0 = not active | U | 3 / 4
133 | 134 | UPS | Alarm: diagnose test failed | 1 = active; 0 = not active | U | 3 / 4
134 | 135 | UPS | Alarm: communication lost | 1 = active; 0 = not active | U | 3 / 4
135 | 136 | UPS | Alarm: awaiting power | 1 = active; 0 = not active | U | 3 / 4
136 | 137 | UPS | Alarm: shutdown pending | 1 = active; 0 = not active | U | 3 / 4
137 | 138 | UPS | Alarm: shutdown imminent | 1 = active; 0 = not active | U | 3 / 4
138 | 139 | UPS | Alarm: test in progress | 1 = active; 0 = not active | U | 3 / 4
143 | 144 | Sensors | Sensormanager/SMTCOM sensor 1 | Analog value | U | 3 / 4
144 | 145 | Sensors | Sensormanager/SMTHCOM sensor 2 | Analog value | U | 3 / 4
145 | 146 | Sensors | Sensormanager sensor 3 | Analog value | U | 3 / 4
146 | 147 | Sensors | Sensormanager sensor 4 | Analog value | U | 3 / 4
147 | 148 | Sensors | Sensormanager sensor 5 | Analog value | U | 3 / 4
148 | 149 | Sensors | Sensormanager sensor 6 | Analog value | U | 3 / 4
149 | 150 | Sensors | Sensormanager sensor 7 | Analog value | U | 3 / 4
150 | 151 | Sensors | Sensormanager sensor 8 | Analog value | U | 3 / 4
50000 | 50001 | SENSORMANAGER I/O | SITEMANAGER/SITEMONITOR/SENSORMANAGER Digital Input 1 | 1 = active (high), 0 = not active (low) | U | 3 / 4
50001 | 50002 | SENSORMANAGER I/O | SITEMANAGER/SITEMONITOR/SENSORMANAGER Digital Input 2 | 1 = active (high), 0 = not active (low) | U | 3 / 4
50002 | 50003 | SENSORMANAGER I/O | SITEMANAGER/SITEMONITOR/SENSORMANAGER Digital Input 3 | 1 = active (high), 0 = not active (low) | U | 3 / 4
50003 | 50004 | SENSORMANAGER I/O | SITEMANAGER/SITEMONITOR/SENSORMANAGER Digital Input 4 | 1 = active (high), 0 = not active (low) | U | 3 / 4
50064 | 50065 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Digital Output 1 | 1 = active (high), 0 = not active (low) | U | 3 / 4
50065 | 50066 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Digital Output 2 | 1 = active (high), 0 = not active (low) | U | 3 / 4
50066 | 50067 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Digital Output 3 | 1 = active (high), 0 = not active (low) | U | 3 / 4
50067 | 50068 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Digital Output 4 | 1 = active (high), 0 = not active (low) | U | 3 / 4
50072 | 50073 | SENSORMANAGER I/O | SM_T_COM/SM_T_H_COM/SENSORMANAGER/SITEMANAGER Analog Input 1 | Analog value | U | 3 / 4
50073 | 50074 | SENSORMANAGER I/O | SM_T_H_COM/SENSORMANAGER/SITEMANAGER Analog Input 2 | Analog value | U | 3 / 4
50074 | 50075 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Analog Input 3 | Analog value | U | 3 / 4
50075 | 50076 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Analog Input 4 | Analog value | U | 3 / 4
50076 | 50077 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Analog Input 5 | Analog value | U | 3 / 4
50077 | 50078 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Analog Input 6 | Analog value | U | 3 / 4
50078 | 50079 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Analog Input 7 | Analog value | U | 3 / 4
50079 | 50080 | SENSORMANAGER I/O | SENSORMANAGER/SITEMANAGER Analog Input 8 | Analog value | U | 3 / 4

## BACnet Objects
BACnet/IP objects
Default UPS object table. Analog Input objects 0-25, Binary Input objects 0-23 (1 = active).
Object type | Instance | Name | Units
Analog Input | 0 | Output Voltage Phase 1 | VOLTS
Analog Input | 1 | Output Voltage Phase 2 | VOLTS
Analog Input | 2 | Output Voltage Phase 3 | VOLTS
Analog Input | 3 | Outpower 1 | PERCENT
Analog Input | 4 | Outpower 2 | PERCENT
Analog Input | 5 | Outpower 3 | PERCENT
Analog Input | 6 | Battery Capacity | PERCENT
Analog Input | 7 | Input Voltage Phase 1 | VOLTS
Analog Input | 8 | Input Voltage Phase 2 | VOLTS
Analog Input | 9 | Input Voltage Phase 3 | VOLTS
Analog Input | 10 | Temperature | DEGREES-CELSIUS
Analog Input | 11 | Autonomy Time minutes | MINUTES
Analog Input | 12 | UPS Status (ASCII HEX) | NO-UNITS
Analog Input | 13 | Battery Voltage | VOLTS
Analog Input | 14 | Input Frequency Phase 1 | HERTZ
Analog Input | 15 | Input Frequency Phase 2 | HERTZ
Analog Input | 16 | Input Frequency Phase 3 | HERTZ
Analog Input | 17 | Powerfail Counter | NO-UNITS
Analog Input | 18 | Sensormanager/SMTCOM sensor 1 | DEGREES-CELSIUS
Analog Input | 19 | Sensormanager/SMTHCOM sensor 2 | PERCENT
Analog Input | 20 | Sensormanager sensor 3 | NO-UNITS
Analog Input | 21 | Sensormanager sensor 4 | NO-UNITS
Analog Input | 22 | Sensormanager sensor 5 | NO-UNITS
Analog Input | 23 | Sensormanager sensor 6 | NO-UNITS
Analog Input | 24 | Sensormanager sensor 7 | NO-UNITS
Analog Input | 25 | Sensormanager sensor 8 | NO-UNITS
Binary Input | 0 | Alarm Battery Bad
Binary Input | 1 | Alarm: On Battery
Binary Input | 2 | Alarm: Battery Low
Binary Input | 3 | Alarm: Battery Depleted
Binary Input | 4 | Alarm: Over temperature
Binary Input | 5 | Alarm: Input Bad
Binary Input | 6 | Alarm: Output Bad
Binary Input | 7 | Alarm: Output Overload
Binary Input | 8 | Alarm: On Bypass
Binary Input | 9 | Alarm: Bypass Bad
Binary Input | 10 | Alarm: Output Off as requested
Binary Input | 11 | Alarm: UPS Off as requested
Binary Input | 12 | Alarm: Charger Failed
Binary Input | 13 | Alarm: UPS Output Off
Binary Input | 14 | Alarm: UPS System Off
Binary Input | 15 | Alarm: Fan Failure
Binary Input | 16 | Alarm: fuse failure
Binary Input | 17 | Alarm: general fault
Binary Input | 18 | Alarm: diagnose test failed
Binary Input | 19 | Alarm: communication lost
Binary Input | 20 | Alarm: awaiting power
Binary Input | 21 | Alarm: shutdown pending
Binary Input | 22 | Alarm: shutdown imminent
Binary Input | 23 | Alarm: test in progress

## Status Codes
UPS status bits (register 109 / BACnet AI 12)
Bitmask: add the decimal values of all active bits. Example: 28 = 4 + 8 + 16 (output on, on battery, battery low).
Bit name | Hex | Decimal | Meaning
UPS_SB_BYPASS_MODE | 0x0001 | 1 | The Bypass is presently engaged on the UPS
UPS_SB_SHUTDOWN | 0x0002 | 2 | The entire UPS has shutdown as commanded
UPS_SB_OUTPUT_ACT | 0x0004 | 4 | Normal State, the output is on
UPS_SB_BACKUP_MODE | 0x0008 | 8 | The UPS is drawing power from the batteries
UPS_SB_BATTERY_LOW | 0x0010 | 16 | The remaining battery run-time is low
UPS_SB_OVER_TEMP | 0x0020 | 32 | A temperature is out of tolerance
UPS_SB_TEST_ACT | 0x0040 | 64 | A test is in progress
UPS_SB_INPUT_HIGH | 0x0080 | 128 | An input condition is out of tolerance
UPS_SB_OUTPUT_HIGH | 0x0100 | 256 | The output load exceeds the UPS output capacity
UPS_SB_INVERTER_FAILURE | 0x0200 | 512 | Inverter error
UPS_SB_BATTERY_BAD | 0x0400 | 1024 | One or more batteries have been determined to require replacement
UPS_SB_ECO_MODE | 0x0800 | 2048 | eco - bypass
UPS_SB_INVERTER_WARN | 0x1000 | 4096 | Inverter warning
UPS_SB_UPS_FAILED | 0x2000 | 8192 | A general fault in the UPS has been detected
UPS_SB_COMM_LOST | 0x4000 | 16384 | A problem has been encountered in the communication to the UPS
UPS_SB_DVG_ALARM | 0x8000 | 32768 | SiteManager/SiteMonitor